## Assumptions
Input metric | Value | Dollar Year (if applicable) | Source
Financial inputs
Average Pre-Tax Cost of Capital | 8.93% |  | Data provided by GMP
Average Post-Tax Cost of Capital | 6.46% |  | Data provided by GMP
Societal Discount rate | 2% |  | CEG assumption
Capitalized A&G | 5.14% |  | Data provided by GMP
MACRS Depreciation Rate |  |  | See table below.
Income Tax rate | 27.71% |  | Data provided by GMP
Inflation rate | 2.2% |  | Data provided by GMP
Property Tax Rate | 1.7% |  | Data provided by GMP
Handy-Whitman escalator | 6.911% |  | Calculated based on data provided by GMP, avg. 10-yr (2015-2025) for North Atlantic Region, Total Distribution Plant
Benefits / Asset lifetime
Expected Useful Life | Years
OH | 47 |  | Data provided by GMP
UG | 56 |  | Data provided by GMP
BESS | 20 |  | Data provided by GMP
MACRS Depreciation Period
OH | 20 |  | Data provided by GMP
UG | 20 |  | Data provided by GMP
BESS | 5 |  | Data provided by GMP
Book Depreciation Period
OH | 50 |  | Data provided by GMP
UG | 50 |  | Data provided by GMP
BESS | 16 |  | Data provided by GMP
Outage Risk Reduction inputs
Mitigation Effectiveness Score
OH | 90% |  | Manufacturer Claim, input provided by GMP
UG | 98% |  | GMP engineering assumption
Applicability Score
OH | 80.33% |  | CEG analysis of GMP data
UG | 83.36% |  | CEG analysis of GMP data
Other inputs
Reduced Pole attachment revenue ($/mi) | 154.6667 | 2021$ | Data provided by GMP
Inspections - UG ($/mi; every 10 years) | 323.33 | 2026$ | Data provided by GMP
Inspections - OH ($/mi; every 10 years) | 476.4 | 2026$ | Data provided by GMP
Unaccelerated timeline for ZOI improvements | 10 |  | years | What pace would these projects be otherwise undertaken at? For the counterfactual baseline analysis
Percent of UG lines vulnerable to vegetation and storms | 6.9% |  | GMP assumption from email extended from tree trimming to storms | <<follow-up on this…I think just for O&M tree trimming. Should not apply to major storm outages since they are just customer poles.
Net install for property tax purposes | 95%
Total Miles / Customers in FY27 budget
OH - 1PH | 19.95 |  | Summary of miles in FY 27 Resilience Projects list provided by GMP
OH - 3PH | 51.32 |  | Summary of miles in FY 27 Resilience Projects list provided by GMP
UG - 1PH | 49.6 |  | Summary of miles in FY 27 Resilience Projects list provided by GMP
Ratio of baseline capital spend | 10% |  | CEG assumption, based on input from GMP
Downstream outage factors
Zone 1 | 100% |  | CEG assumption, based on engineering input from GMP
Zone 2 | 100% |  | CEG assumption, based on engineering input from GMP
Zone 3 | 50% |  | CEG assumption, based on engineering input from GMP
O&M Cost Input Assumptions per mile
Tree trimming costs, annualized
7-yr Cycle, Annualized costs, Baseline cost per mile | 1869.6903 | 2026$ | Data provided by GMP
7-yr Cycle, Annualized costs, Mitigation cost per mile | 129.1491 | 2026$ | Data provided by GMP
Danger Tree and Tickets cost per mile
Tickets - Baseline cost per mile | 262.3659 | 2025$ | Data provided by GMP
Tickets - UG cost per mile | 65.5915 | 2025$ | Data provided by GMP
Danger Tree - Baseline cost per mile | 56.727 | 2025$ | Data provided by GMP
Danger Tree - UG cost per mile | 5.6727 | 2025$ | Data provided by GMP
Average Storm Outage Cost per FY, 2015-2024 | 24277878.0059 | 2025$ | CEG analysis of Data provided by GMP
Annual increase (linear) | 2663245.8869 | 2025$ | CEG analysis of Data provided by GMP
Avg storm cost per mile OH | 2415.7093 | 2025$ | Row 60 divided by row 64 (total system miles OH)
Avg annual storm cost increase per mile OH | 264.9996 | 2025$ | Row 61 divided by row 64 (total system miles OH)
Total system miles OH | 10050 |  | Data provided by GMP
Average Restoration cost per incident | 472 | 2025$ | Data provided by GMP
Average Non-storm incident percentage | 54.65% |  | Data provided by GMP
MACRS table, half-year convention |  |  | Data provided by GMP
Year | 20-year
1 | 3.75%
2 | 7.219%
3 | 6.677%
4 | 6.177%
5 | 5.713%
6 | 5.285%
7 | 4.888%
8 | 4.522%
9 | 4.462%
10 | 4.461%
11 | 4.462%
12 | 4.461%
13 | 4.462%
14 | 4.461%
15 | 4.462%
16 | 4.461%
17 | 4.462%
18 | 4.461%
19 | 4.462%
20 | 4.461%
21 | 2.231%

## Figures_Testimony
Baseline Scenario Costs and Benefits Summary and BCR
Project Type | Line Phases | Total FY2027 CAPEX (Fully Loaded) | NPV Total Costs (Sum of a-e) | (a) NPV Utility CAPEX | (b) NPV Property Tax from New CAPEX | (c) NPV Storm Restoration Costs | (d) NPV Non-Storm Restoration Costs | (e) NPV O&M Costs (Veg Mng and Inspections)
OH Spacer | 1-Phase | 1003129.1 | 12461947.854 | 9657187.1672 | 1998373.1226 | 716777.0864 | 89610.4778 | 0
OH Spacer | 3-Phase | 3612272.3 | 44825609.3994 | 34775573.453 | 7196150.4015 | 1843859.6529 | 1010025.892 | 0
UG CIC | 1-Phase | 2984286.2 | 37488972.4761 | 28729911.6273 | 5945114.4744 | 1499383.5858 | 240736.6801 | 1073826.1085
Total |  | 7599687.6 | 94776529.7296 | 73162672.2475 | 15139637.9985 | 4060020.3252 | 1340373.0499 | 1073826.1085
Mitigation Scenario Costs and Benefits Summary and BCR
Project Type | Line Phases | Total FY2027 CAPEX (Fully Loaded) | NPV Total Costs (Sum of a-e) | (a) NPV Utility CAPEX | (b) NPV Property Tax from New CAPEX | (c) NPV Storm Restoration Costs | (d) NPV Non-Storm Restoration Costs | (e) NPV O&M Costs (Veg Mng and Inspections)
OH Spacer | 1-Phase | 10031291 | 14165553.5472 | 11525963.1869 | 2398181.5586 | 194607.7914 | 46801.0103 | 0
OH Spacer | 3-Phase | 36122723 | 51169029.4542 | 41505044.1173 | 8635862.3378 | 500615.1305 | 527507.8687 | 0
UG CIC | 1-Phase | 29842862 | 41952140.4725 | 34289477.6758 | 7134535.4556 | 102448.817 | 99360.8603 | 326317.6639
Total |  | 75996876 | 107286723.474 | 87320484.98 | 18168579.352 | 797671.7388 | 673669.7393 | 326317.6639
Overall resilience BCA for FY27 ZOI Resilience Projects
Project Type | Line Phases | (A) NPV Total Incremental Benefits | (B) NPV Total Incremental Costs | (C) (A ⁒ B) Benefit Cost Ratio
OH Spacer | 1-Phase | 13763473.397 | 2268584.4558 | 6.067
OH Spacer | 3-Phase | 222896674.5681 | 8169182.6006 | 27.2851
UG CIC | 1-Phase | 39194096.2685 | 6748987.0296 | 5.8074
Total |  | 275854244.2335 | 17186754.086 | 16.0504
Overall resilience BCA for Integrated Energy Storage Pilot
Project Type | (A) NPV Total Incremental Benefits | (B) NPV Total Incremental Costs | (C) (A ⁒ B) Benefit Cost Ratio
Integrated Energy Storage Pilot | 6615432.3485 | 5941546.1689 | 1.1134
Table - FY27 T&D Resilience Projects - Overall NPV of Net Benefits Broken out by category
Project Type | Line Phases | NPV Reduced Storm Damages | NPV Reduced Non-Storm Damages | NPV Lower O&M Expenditures | NPV Customer Resilience Value - Circuit Hardening | NPV Customer Resilience Value - Feeder-Back Up | NPV Line Loss Reduction
OH Spacer | 1-Phase | 522169.2951 | 42809.4675 | 0 | 13196382.8255 | 0 | 2111.8089
OH Spacer | 3-Phase | 1343244.5224 | 482518.0233 | 0 | 182568584.3178 | 37855624.742 | 646702.9625
UG CIC | 1-Phase | 1396934.7689 | 141375.8198 | 747508.4446 | 36758715.6449 | 0 | 149561.5903
Total |  | 3262348.5864 | 666703.3106 | 747508.4446 | 232523682.7882 | 37855624.742 | 798376.3617
Integrated Storage Pilot - NPV Costs
Program | NPV Total Incremental Cost | NPV Capital Carrying Costs | NPV End of Life Removal | NPV O&M | NPV Software Fees | NPV RTE Losses (Credit)
Integrated Energy Storage Pilot | 5941546.1689 | 5614596.5995 | 28341.4307 | 10355.1952 | 67326.9434 | 220926.0001
Integrated Energy Storage Pilot - NPV Benefits
(A) Program | NPV Total Incremental Benefit | NPV ISO-NE FCM Capacity Reductions | NPV RNS Transmission Charge Reduction | NPV T&D Deferral Value | NPV Avoided Wholesale Energy | NPV RTE Losses (Revenue under Rate 1) | NPV Frequency Regulation Revenue | NPV DASI | Tier 3 RES Value
Integrated Energy Storage Pilot | 6454954.0606 | 1923548.7182 | 3237562.8171 | 274641.5992 | 459063.7424 | 220926.0001 | 183704.5778 | 21599.9585 | 133906.6473
Updated with final - updated in Testimony
Project Type | Line Phases | Circuit Miles Treated | Capital Cost Estimate
OH Spacer | 1-Phase | 19.95 | 10031291
OH Spacer | 3-Phase | 51.32 | 36122723
UG CIC | 1-Phase | 49.6 | 29842862
Total |  | 120.87 | 75996876
1

## FY27 Resiliency Projects
Final FY27 Resilience Projects List - With Subtotals by Project Type and Line Phase
Mitigation Type | Phase | Feeder ID | District | Project Number | Project Name | 1Ph or 3PH | OH/UG | Distance | Cost Estimate
Overhead Spacer Cable | Three Phase | BV-G43 | Springfield | 203031 | 203031: L43 P57 BV-G43 Mainline | 3PH | OH | 3.7 | 2754059
|  | BV-G44 | Springfield | 199623 | 199623: BV Sub to L4 P126 | 3PH | OH | 1.5 | 1109903
|  | BV-G44 | Springfield | 199973 | 199973: L41 VT Route 106 - Spacer | 3PH | OH | 2.1 | 1553533
|  | BV-G44 | Springfield | 204892 | 204892: L4-L43 poles 1 through 36 | 3PH | OH | 1.65 | 1214917
|  | CS-G34 | Royalton | 203325 | 203325: Chelsea L6 Zone 2 L6 P327 | 3PH | OH | 2.7 | 2009727
|  | CS-G34 | Royalton | 205188 | 205188: L.6 P .251X - P166 | 3PH | OH | 2.8 | 2073314
|  | CS-G34 | Royalton | 205534 | 205534: L6 P126 to P66 | 3PH | OH | 1.9 | 1400395
|  | CV-G65 | Springfield | 175351 | 175351: Cavendish line 2 | 3PH | OH | 1.2 | 917484
|  | CV-G65 | Springfield | 202178 | 202178: CV-G65 L2P206 | 3PH | OH | 5.5 | 4138361
|  | DM-G6 | Brattleboro | 199297 | 199297: L66 P15-1 to L62 P140 | 3PH | OH | 3.3 | 2456234
|  | DM-G6 | Brattleboro | 204888 | 204888: Rt 30-Main Line feeder | 3PH | OH | 5 | 3762144
|  | DM-G6 | Brattleboro | 204889 | 204889: L6-Dover Rd-L61 P1-P121 | 3PH | OH | 4 | 940532
|  | EL-G40 | White River Jct | 197817 | 197817: ELY-129 G40 Zone 1 LC | 3PH | OH | 2.4 | 1782012
|  | EL-G40 | White River Jct | 199494 | 199494: L3P52 | 3PH | OH | 3 | 2227005
|  | EL-G40 | White River Jct | 204106 | 204106: RTE 113 L3 P.141 to P192 | 3PH | OH | 1.7 | 1251737
|  | EL-G40 | White River Jct | 204107 | 204107: Beanville Rd L37 P.X2 P21 | 3PH | OH | 1.12 | 822502
|  | SB-G91 | Rutland | 204891 | 204891: WO212564 - L8 P298 thru P215 | 3PH | OH | 3.3 | 2418666
|  | TH-G16 | White River Jct | 203716 | 203716: RTE 5 L1 P.137 (tag: 4902 | 3PH | OH | 1.5 | 1110638
|  | TH-G16 | White River Jct | 203723 | 203723: RTE 113 L1 Start at P.156 | 3PH | OH | 0.8 | 587651
|  | TH-G16 | White River Jct | 203724 | 203724: RTE 113 L1 P.217 | 3PH | OH | 2.15 | 1591909
[5 empty] | Subtotal - Overhead Spacer Cable - Three Phase |  |  | 51.32 | 36122723
| Single Phase | DM-G6 | Brattleboro | 199616 | 199616: Newfane L66 P1-105 | 1PH | OH | 2.5 | 1258653
|  | DM-G6 | Brattleboro | 199621 | 199621: Brookline L62 P140-195 | 1PH | OH | 4.75 | 2385224
|  | CH-G11 | Springfield | 201152 | 201152: L342 TOWNSHEND RD | 1PH | OH | 5.2 | 2617704
|  | BV-G44 | Springfield | 204901 | 204901: L434 P3 | 1PH | OH | 4.5 | 2259492
|  | SB-G91 | Rutland | 204902 | 204902: L88 Rt100A, Spacer and CI | 1PH | OH | 3 | 1510218
[5 empty] | Subtotal - Overhead Spacer Cable - Single Phase |  |  | 19.95 | 10031291
Underground | Single Phase | BV-G43 | Springfield | 201153 | 201153: L438 BROWNSVILLE - CIC | 1PH | UG | 1.5 | 1442345
|  | BV-G43 | Springfield | 204899 | 204899: L43 Brook Rd | 1PH | UG | 1.5 | 1441983
|  | BV-G44 | Springfield | 204893 | 204893: L44 P65 thru P93 | 1PH | UG | 1.75 | 1012095
|  | CH-G11 | Springfield | 204900 | 204900: L3135 Stage Rd | 1PH | UG | 5 | 2891675
|  | CS-G34 | Royalton | 204898 | 204898: L61 P1 - P47 Russell Rd W | 1PH | UG | 3.1 | 1797640
|  | CV-G65 | Springfield | 201142 | 201142: L208 HIGH ST. - CIC | 1PH | UG | 1.9 | 1076503
|  | CV-G65 | Springfield | 204894 | 204894: L209 P1-P53 Tarbel Rd-Kna | 1PH | UG | 2.5 | 1445839
|  | DM-G6 | Brattleboro | 201143 | 201143: L61 DOVER RD. - CIC | 1PH | UG | 4.25 | 2458013
|  | DM-G6 | Brattleboro | 201149 | 201149: L6 VT RT 30 - CIC | 1PH | UG | 4.35 | 2515767
|  | DM-G6 | Brattleboro | 203953 | 203953: L.9-P.61 Quarry Rd | 1PH | UG | 2 | 1156671
|  | DM-G6 | Brattleboro | 203954 | 203954: L633-Timson Hl Rd/Baker B | 1PH | UG | 2.75 | 1590420
|  | DM-G6 | Brattleboro | 204895 | 204895: L65-South Wardsboro Rd | 1PH | UG | 3.35 | 1958291
|  | DM-G6 | Brattleboro | 204896 | 204896: L94-Leonard Rd-Stickney B | 1PH | UG | 3 | 1739649
|  | DM-G6 | Brattleboro | 204897 | 204897: L911-P16 to End Hague Rd | 1PH | UG | 1 | 575258
|  | EL-G40 | White River Jct | 204108 | 204108: S.Vershire Rd L37 21 - 53 | 1PH | UG | 2 | 1159766
|  | SH-G35 | Royalton | 199309 | 199309: Fay Brook Rd. | 1PH | UG | 1.2 | 694311
|  | SH-G35 | Royalton | 199373 | 199373: FAY BROOK RD P.44 -P.75 | 1PH | UG | 1.5 | 867921
|  | SH-G35 | Royalton | 199498 | 199498: Brk Rd. P.75-L.81P.76 | 1PH | UG | 3 | 1735452
|  | SH-G35 | Royalton | 199569 | 199569: Brook Rd. P.76 to 50X | 1PH | UG | 1.7 | 978528
|  | TH-G16 | White River Jct | 203725 | 203725: Tucker Hill L1 294–333 | 1PH | UG | 2.25 | 1304735
[5 empty] | Subtotal - Strategic Undergrounding - Single Phase |  |  | 49.6 | 29842862
[5 empty] | Total Overall Portfolio - T&D OH and UG |  |  | 120.87 | 75996876

## Results
Baseline Scenario Costs and Benefits Summary and BCR | [14 empty] | Budget - Mitigation Projects in T&D Resilience Initiatives
Program | Project Type | Total FY2027 Costs | NPV Total Costs | NPV Total Benefits | NPV Utility CAPEX | NPV Utility Storm Damage Restoration Costs | NPV Net New Property Tax | NPV Utility O&M Costs | NPV Customer Cost of Outages - Res | NPV Customer Cost of Outages - Nonres | NPV Utility Non-Storm Damage Restoration Costs | Value of Decreased Line Losses - Line Capacity Improvements | NPV Feeder Backup Value - Baseline - Res | NPV Feeder Backup Value - Baseline - NonRes | Project Type | Line Phase | Cost Estimate | Total Circuit Miles | All in Total $/mi
OH | 1-Phase | 1003129.1 | 12461947.854 | 23998786.9688 | 9657187.1672 | 716777.0864 | 1998373.1226 | 0 | 760588.6157 | 23238198.3532 | 89610.4778 | 4406.8167 | 0 | 0 | OH | 1PH | 10031291 | 19.95 | 502821.604
OH | 3-Phase | 3612272.3 | 44825609.3994 | 358325938.8047 | 34775573.453 | 1843859.6529 | 7196150.4015 | 0 | 10951522.3386 | 321192251.1395 | 1010025.892 | 230539.1377 | 1514386.0458 | 24667779.2808 | OH | 3PH | 36122723 | 51.32 | 703872.233
UG | 1-Phase | 2984286.2 | 37488972.4761 | 57595662.1118 | 28729911.6273 | 1499383.5858 | 5945114.4744 | 1073826.1085 | 2039295.2274 | 55556366.8844 | 240736.6801 | 56692.98 | 0 | 0 | UG | 1PH | 29842862 | 49.6 | 601670.6048
Total |  | 7599687.6 | 94776529.7296 | 439920387.8854 | 73162672.2475 | 4060020.3252 | 15139637.9985 | 1073826.1085 | 13751406.1817 | 399986816.3771 | 1340373.0499 | 291638.9344 | 1514386.0458 | 24667779.2808 | Total |  | 75996876 | 120.87 | 628748.8707
Mitigation Scenario Costs and Benefits Summary and BCR
Program | Project Type | Total FY2027 Costs | NPV Total Costs | NPV Total Benefits | NPV Utility CAPEX | NPV Utility Storm Damage Restoration Costs | NPV Net New Property Tax | NPV Utility O&M Costs | NPV Customer Cost of Outages - Res | NPV Customer Cost of Outages - Nonres | NPV Utility Non-Storm Damage Restoration Costs | Value of Decreased Line Losses - Line Capacity Improvements | NPV Feeder Backup Value - Mitigation - Res | NPV Feeder Backup Value - MItigation - NonRes
OH | 1-Phase | 10031291 | 14165553.5472 | 10802404.1433 | 11525963.1869 | 194607.7914 | 2398181.5586 | 0 | 463089.311 | 10339314.8323 | 46801.0103 | 6518.6256 | 0 | 0
OH | 3-Phase | 36122723 | 51169029.4542 | 213612979.2289 | 41505044.1173 | 500615.1305 | 8635862.3378 | 0 | 6667905.3953 | 142907283.765 | 527507.8687 | 877242.1002 | 2229963.638 | 61807826.4306
UG | 1-Phase | 29842862 | 41952140.4725 | 20836946.4669 | 34289477.6758 | 102448.817 | 7134535.4556 | 326317.6639 | 996600.5796 | 19840345.8874 | 99360.8603 | 206254.5703 | 0 | 0
Total |  | 75996876 | 107286723.474 | 245252329.8391 | 87320484.98 | 797671.7388 | 18168579.352 | 326317.6639 | 8127595.2858 | 173086944.4847 | 673669.7393 | 1090015.2961 | 2229963.638 | 61807826.4306
Final BCR Table -- T&D Resilience Projects
|  |  | Cost Categories |  |  | Benefit Categories
(A) Program | (B) Project Type | (C) NPV total Net Incremental Cost | NPV Total Net Incremental CAPEX | NPV Total Net Property Taxes | (D) NPV total Net Benefits | (E) Reduced Storm Damages | (F) Lower O&M Expenditures | (G) Customer Resilience Value - Res | (H) Customer Resilience Value - Nonres | Line Losses Reduction Value | Reduced Non-Storm Damages | Feeder Backup Customer Resilience Value - Res | Feeder Backup Customer Resilience Value - Nonres | (I) (D ⁒ C) Benefit Cost Ratio (including all resilience value)
OH | 1-Phase | 2268584.4558 | 1868776.0197 | 399808.4361 | 13763473.397 | 522169.2951 | 0 | 297499.3047 | 12898883.5208 | 2111.8089 | 42809.4675 | 0 | 0 | 6.067
OH | 3-Phase | 8169182.6006 | 6729470.6643 | 1439711.9362 | 222896674.5681 | 1343244.5224 | 0 | 4283616.9433 | 178284967.3745 | 646702.9625 | 482518.0233 | 715577.5922 | 37140047.1498 | 27.2851
UG | 1-Phase | 6748987.0296 | 5559566.0485 | 1189420.9812 | 39194096.2685 | 1396934.7689 | 747508.4446 | 1042694.6479 | 35716020.997 | 149561.5903 | 141375.8198 | 0 | 0 | 5.8074
Total |  | 17186754.086 | 14157812.7325 | 3028941.3535 | 275854244.2335 | 3262348.5864 | 747508.4446 | 5623810.8958 | 226899871.8924 | 798376.3617 | 666703.3106 | 715577.5922 | 37140047.1498 | 16.0504
Final BCR Table -- Integrated Energy Storage Pilot
Benefit Categories
(A) Program | (C) NPV total Net Incremental Cost | (D) NPV total Net Benefits | (E) Utility System Avoided Costs | (F) Customer Resilience Value | (G) (D ⁒ C) Benefit Cost Ratio | BCR Without Customer Resilience Value
Integrated Energy Storage Pilot | 5941546.1689 | 6615432.3485 | 6454954.0606 | 160478.2879 | 1.1134 | 1.0864

## Costs_Baseline
[5 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66
T&D Resilience Projects - Overhead Spacer Cable (OH) - Detailed Annual Cost Calcs
Phase | Type | Cost Bucket | Cost Category | Notes | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093
1PH | OH | CAPEX | Plant in Service | Handled in Rev Req't Baseline tab
1PH | OH | CAPEX | Cumulative Depreciation | Handled in Rev Req't Baseline tab
1PH | OH | CAPEX | ADIT | Handled in Rev Req't Baseline tab
1PH | OH | CAPEX | Net Plant in Service | Handled in Rev Req't Baseline tab
1PH | OH | CAPEX | Net Rate Base | Handled in Rev Req't Baseline tab
1PH | OH | CAPEX | Average Rate Base | Handled in Rev Req't Baseline tab
1PH | OH | CAPEX | Capitalized A&G | Handled in Rev Req't Baseline tab
1PH | OH | CAPEX | Pre-tax Return on Rate Base |  |  | 88466.3986 | 176222.3748 | 262888.9569 | 348571.5267 | 433368.1017 | 517369.9182 | 600661.9027 | 683323.1535 | 765392.676 | 846865.0243 | 817753.7483 | 788901.8654 | 760766.7562 | 733203.3956 | 706075.6044 | 679255.3182 | 652621.9939 | 626062.004 | 599511.2246 | 572960.4452 | 546686.6102 | 521249.5774 | 496944.7009 | 473796.8882 | 451831.5945 | 431074.8354 | 411553.1987 | 393293.8569 | 376324.5807 | 360673.7513 | 346026.1028 | 331715.3153 | 317404.5278 | 303093.7403 | 288782.9528 | 274472.1653 | 260161.3778 | 245850.5903 | 231539.8028 | 217229.0153 | 202918.2278 | 188607.4403 | 174296.6528 | 159985.8653 | 145675.0778 | 131364.2904 | 117053.5029 | 102742.7154 | 88431.9279 | 74121.1404 | 60457.8778 | 48103.9105 | 37088.0431 | 27439.7138 | 19189.0083 | 12366.6744 | 7004.1363 | 3133.5095 | 787.616 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11
1PH | OH | CAPEX | Depreciation Expense |  |  | 20062.582 | 40566.5408 | 61521.5867 | 82937.6436 | 104824.8538 | 127193.5826 | 150054.4234 | 173418.2027 | 197295.9851 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 201636.4968 | 181132.538 | 160177.4921 | 138761.4352 | 116874.225 | 94505.4963 | 71644.6554 | 48280.8761 | 24403.0937 | 0 | 0 | 0 | 0
1PH | OH | O&M | Outage Restoration - Major/Minor Storm |  |  | 51950.1286 | 52825.7075 | 52971.1491 | 52392.8582 | 51096.4752 | 49086.8825 | 46368.2115 | 42943.8482 | 38816.4385 | 33987.8931 | 34735.6267 | 35499.8105 | 36280.8063 | 37078.9841 | 37894.7217 | 38728.4056 | 39580.4305 | 40451.2 | 41341.1264 | 42250.6312 | 43180.1451 | 44130.1083 | 45100.9706 | 46093.192 | 47107.2422 | 48143.6015 | 49202.7608 | 50285.2215 | 51391.4964 | 52522.1093 | 53677.5957 | 54858.5028 | 56065.3899 | 57298.8285 | 58559.4027 | 59847.7095 | 61164.3592 | 62509.9751 | 63885.1945 | 65290.6688 | 66727.0635 | 68195.0589 | 69695.3502 | 71228.6479 | 72795.6782 | 74397.1831 | 76033.9211 | 77706.6674 | 79416.214 | 81163.3708 | 82948.9649 | 84773.8421 | 86638.8667 | 88544.9217 | 90492.91 | 92483.754 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | OH | O&M | Routine (non-storm) Restoration costs |  |  | 7824.3993 | 7400.8116 | 6981.6255 | 6566.6218 | 6155.5838 | 5748.2971 | 5344.5495 | 4944.1311 | 4546.8338 | 4152.4515 | 4243.8054 | 4337.1691 | 4432.5869 | 4530.1038 | 4629.7661 | 4731.6209 | 4835.7166 | 4942.1023 | 5050.8286 | 5161.9468 | 5275.5096 | 5391.5709 | 5510.1854 | 5631.4095 | 5755.3005 | 5881.9171 | 6011.3193 | 6143.5683 | 6278.7268 | 6416.8588 | 6558.0297 | 6702.3064 | 6849.7571 | 7000.4517 | 7154.4617 | 7311.8598 | 7472.7208 | 7637.1206 | 7805.1373 | 7976.8503 | 8152.341 | 8331.6925 | 8514.9897 | 8702.3195 | 8893.7705 | 9089.4335 | 9289.401 | 9493.7679 | 9702.6307 | 9916.0886 | 10134.2426 | 10357.1959 | 10585.0542 | 10817.9254 | 11055.9198 | 11299.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | OH | O&M | Pole Inspections | Not included as no change
1PH | OH | O&M | Veg Mng - Tree Trimming | Not included as no change
1PH | OH | O&M | Veg Mng - Tickets | Not included as no change
1PH | OH | O&M | Veg Mng - Danger Trees | Not included as no change
1PH | OH | O&M | Property Taxes |  |  | 16200.535 | 32757.4817 | 49678.6813 | 66972.1472 | 84646.0694 | 102708.8179 | 121168.9469 | 140035.1987 | 140035.1987 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 179022.0061 | 162821.4712 | 146264.5244 | 129343.3249 | 112049.8589 | 94375.9367 | 76313.1882 | 57853.0593 | 38986.8075 | 19705.4981 | 0 | 0 | 0 | 0
1PH | OH | O&M | Reduced pole attachment revenue | Not included as no change
|  | Total Costs impacting revenue requirement |  |  |  | 184504.0435 | 309772.9164 | 434041.9995 | 557440.7975 | 680091.0839 | 802107.4983 | 923598.0339 | 1044664.5341 | 1146087.1321 | 1285726.4538 | 1257454.2654 | 1229459.93 | 1202201.2343 | 1175533.5684 | 1149321.1772 | 1123436.4297 | 1097759.226 | 1072176.3913 | 1046624.2645 | 1021094.1081 | 995863.3499 | 971492.3415 | 948276.9419 | 926242.5746 | 905415.2222 | 885821.4391 | 867488.3637 | 850443.7317 | 834715.8888 | 820333.8044 | 806982.8132 | 793997.2094 | 781040.7597 | 768114.1055 | 755217.9021 | 742352.8197 | 729519.5427 | 716718.7709 | 703951.2196 | 691217.6194 | 678518.7173 | 665855.2767 | 653228.0777 | 640637.9177 | 628085.6115 | 615571.9919 | 603097.9099 | 590664.2355 | 578271.8576 | 565921.6847 | 517999.0532 | 470632.011 | 423832.781 | 377613.855 | 331987.9998 | 286968.2629 | 136501.851 | 90401.1931 | 44896.2078 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11
|  | Subtotal | CAPEX |  |  | 108528.9806 | 216788.9156 | 324410.5436 | 431509.1703 | 538192.9555 | 644563.5008 | 750716.3261 | 856741.3562 | 962688.6611 | 1068564.1031 | 1039452.8271 | 1010600.9442 | 982465.835 | 954902.4744 | 927774.6832 | 900954.397 | 874321.0728 | 847761.0829 | 821210.3034 | 794659.524 | 768385.689 | 742948.6562 | 718643.7797 | 695495.967 | 673530.6733 | 652773.9143 | 633252.2775 | 614992.9357 | 598023.6595 | 582372.8302 | 567725.1816 | 553414.3941 | 539103.6066 | 524792.8191 | 510482.0316 | 496171.2441 | 481860.4566 | 467549.6691 | 453238.8816 | 438928.0941 | 424617.3066 | 410306.5191 | 395995.7317 | 381684.9442 | 367374.1567 | 353063.3692 | 338752.5817 | 324441.7942 | 310131.0067 | 295820.2192 | 262094.3746 | 229236.4485 | 197265.5352 | 166201.149 | 136063.2333 | 106872.1707 | 78648.7917 | 51414.3856 | 25190.7097 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11
|  | Subtotal | O&M Total |  |  | 75975.0628 | 92984.0009 | 109631.4559 | 125931.6272 | 141898.1284 | 157543.9975 | 172881.7079 | 187923.1779 | 183398.4709 | 217162.3507 | 218001.4383 | 218858.9858 | 219735.3993 | 220631.094 | 221546.4939 | 222482.0327 | 223438.1532 | 224415.3085 | 225413.9611 | 226434.5841 | 227477.6609 | 228543.6853 | 229633.1622 | 230746.6076 | 231884.5489 | 233047.5248 | 234236.0862 | 235450.796 | 236692.2293 | 237960.9743 | 239257.6316 | 240582.8153 | 241937.1531 | 243321.2864 | 244735.8705 | 246181.5755 | 247659.0861 | 249169.1018 | 250712.3379 | 252289.5252 | 253901.4106 | 255548.7575 | 257232.3461 | 258952.9736 | 260711.4548 | 262508.6227 | 264345.3283 | 266222.4414 | 268140.8509 | 270101.4655 | 255904.6787 | 241395.5625 | 226567.2458 | 211412.7061 | 195924.7665 | 180096.0923 | 57853.0593 | 38986.8075 | 19705.4981 | 0 | 0 | 0 | 0
|  | Subtotal | O&M - Cost Savings (minus property tax) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Subtotal | O&M - Storm Damage Reductions |  |  | 51950.1286 | 52825.7075 | 52971.1491 | 52392.8582 | 51096.4752 | 49086.8825 | 46368.2115 | 42943.8482 | 38816.4385 | 33987.8931 | 34735.6267 | 35499.8105 | 36280.8063 | 37078.9841 | 37894.7217 | 38728.4056 | 39580.4305 | 40451.2 | 41341.1264 | 42250.6312 | 43180.1451 | 44130.1083 | 45100.9706 | 46093.192 | 47107.2422 | 48143.6015 | 49202.7608 | 50285.2215 | 51391.4964 | 52522.1093 | 53677.5957 | 54858.5028 | 56065.3899 | 57298.8285 | 58559.4027 | 59847.7095 | 61164.3592 | 62509.9751 | 63885.1945 | 65290.6688 | 66727.0635 | 68195.0589 | 69695.3502 | 71228.6479 | 72795.6782 | 74397.1831 | 76033.9211 | 77706.6674 | 79416.214 | 81163.3708 | 82948.9649 | 84773.8421 | 86638.8667 | 88544.9217 | 90492.91 | 92483.754 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Cost Bucket | Cost Category | Notes | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093
Phase | Type
3PH | OH | CAPEX | Plant in Service | Handled in Rev Req't Baseline tab
3PH | OH | CAPEX | Cumulative Depreciation | Handled in Rev Req't Baseline tab
3PH | OH | CAPEX | ADIT | Handled in Rev Req't Baseline tab
3PH | OH | CAPEX | Net Plant in Service | Handled in Rev Req't Baseline tab
3PH | OH | CAPEX | Net Rate Base | Handled in Rev Req't Baseline tab
3PH | OH | CAPEX | Average Rate Base | Handled in Rev Req't Baseline tab
3PH | OH | CAPEX | Capitalized A&G | Handled in Rev Req't Baseline tab
3PH | OH | CAPEX | Pre-tax Return on Rate Base |  |  | 318567.8905 | 634577.5465 | 946664.2898 | 1255207.6004 | 1560560.4399 | 1863051.3505 | 2162986.1528 | 2460649.6805 | 2756182.3918 | 3049564.6763 | 2944734.8433 | 2840839.0863 | 2739524.4342 | 2640268.6514 | 2542581.3562 | 2446001.3877 | 2350094.6698 | 2254452.0294 | 2158842.5559 | 2063233.0824 | 1968620.8873 | 1877022.0203 | 1789500.0532 | 1706144.6776 | 1627047.5586 | 1552302.3779 | 1482004.8781 | 1416252.9081 | 1355146.4697 | 1298787.7645 | 1246041.5176 | 1194508.309 | 1142975.1003 | 1091441.8916 | 1039908.6829 | 988375.4742 | 936842.2655 | 885309.0568 | 833775.8481 | 782242.6394 | 730709.4307 | 679176.222 | 627643.0133 | 576109.8046 | 524576.5959 | 473043.3872 | 421510.1785 | 369976.9698 | 318443.7611 | 266910.5524 | 217709.0837 | 173222.3933 | 133554.2064 | 98810.5299 | 69099.7032 | 44532.4489 | 25221.9256 | 11283.7814 | 2836.2087 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11
3PH | OH | CAPEX | Depreciation Expense |  |  | 72245.446 | 146080.2918 | 221539.5042 | 298658.8193 | 377474.7594 | 458024.6501 | 540346.6384 | 624479.7104 | 710463.71 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 726093.9117 | 652259.0658 | 576799.8534 | 499680.5383 | 420864.5983 | 340314.7076 | 257992.7193 | 173859.6472 | 87875.6476 | 0 | 0 | 0 | 0
3PH | OH | O&M | Outage Restoration - Major/Minor Storm |  |  | 133638.1253 | 135890.4918 | 136264.6301 | 134777.0167 | 131442.1607 | 126272.6221 | 119279.0284 | 110470.0897 | 99852.6127 | 87431.5124 | 89355.0057 | 91320.8158 | 93329.8737 | 95383.131 | 97481.5599 | 99626.1542 | 101817.9296 | 104057.924 | 106347.1983 | 108686.8367 | 111077.9471 | 113521.6619 | 116019.1385 | 118571.5596 | 121180.1339 | 123846.0968 | 126570.7109 | 129355.2666 | 132201.0824 | 135109.5063 | 138081.9154 | 141119.7175 | 144224.3513 | 147397.2871 | 150640.0274 | 153954.108 | 157341.0983 | 160802.6025 | 164340.2598 | 167955.7455 | 171650.7719 | 175427.0889 | 179286.4848 | 183230.7875 | 187261.8648 | 191381.6258 | 195592.0216 | 199895.0461 | 204292.7371 | 208787.1773 | 213380.4952 | 218074.8661 | 222872.5132 | 227775.7084 | 232786.774 | 237908.0831 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3PH | OH | O&M | Routine (non-storm) Restoration costs |  |  | 88191.0915 | 83416.7113 | 78691.9423 | 74014.3142 | 69381.3844 | 64790.7366 | 60239.9797 | 55726.7466 | 51248.6926 | 46803.4946 | 47833.1715 | 48885.5013 | 49960.9823 | 51060.1239 | 52183.4467 | 53331.4825 | 54504.7751 | 55703.8801 | 56929.3655 | 58181.8116 | 59461.8114 | 60769.9713 | 62106.9106 | 63473.2627 | 64869.6744 | 66296.8073 | 67755.337 | 69245.9545 | 70769.3654 | 72326.2915 | 73917.4699 | 75543.6542 | 77205.6146 | 78904.1382 | 80640.0292 | 82414.1098 | 84227.2203 | 86080.2191 | 87973.9839 | 89909.4116 | 91887.4186 | 93908.9418 | 95974.9385 | 98086.3872 | 100244.2877 | 102449.662 | 104703.5546 | 107007.0328 | 109361.1875 | 111767.1337 | 114226.0106 | 116738.9828 | 119307.2405 | 121931.9997 | 124614.5037 | 127356.0228 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3PH | OH | O&M | Pole Inspections | Not included as no change
3PH | OH | O&M | Veg Mng - Tree Trimming | Not included as no change
3PH | OH | O&M | Veg Mng - Tickets | Not included as no change
3PH | OH | O&M | Veg Mng - Danger Trees | Not included as no change
3PH | OH | O&M | Property Taxes |  |  | 58338.1976 | 117959.8356 | 178893.1497 | 241166.9966 | 304810.8682 | 369854.9049 | 436329.9105 | 504267.3661 | 504267.3661 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 644659.0313 | 586320.8337 | 526699.1957 | 465765.8816 | 403492.0347 | 339848.1631 | 274804.1264 | 208329.1208 | 140391.6652 | 70959.5855 | 0 | 0 | 0 | 0
3PH | OH | O&M | Reduced pole attachment revenue | Not included as no change
|  | Total Costs impacting revenue requirement |  |  |  | 670980.751 | 1117924.877 | 1562053.5161 | 2003824.7472 | 2443669.6125 | 2881994.2642 | 3319181.7097 | 3755593.5934 | 4122014.7733 | 4626798.0723 | 4524921.4095 | 4424043.7924 | 4325813.6793 | 4229710.2953 | 4135244.7517 | 4041957.4133 | 3949415.7635 | 3857212.2225 | 3765117.5087 | 3673100.1196 | 3582159.0347 | 3494312.0425 | 3410624.4912 | 3331187.8888 | 3256095.7559 | 3185443.671 | 3119329.315 | 3057852.5181 | 3001115.3066 | 2949221.9512 | 2901039.2919 | 2854170.0697 | 2807403.4552 | 2760741.7057 | 2714187.1284 | 2667742.0809 | 2621408.973 | 2575190.2673 | 2529088.4807 | 2483106.1854 | 2437246.0101 | 2391510.6416 | 2345902.8256 | 2300425.3682 | 2255081.1374 | 2209873.064 | 2164804.1436 | 2119877.4376 | 2075096.0747 | 2030463.2523 | 1857730.3348 | 1686994.5038 | 1518299.695 | 1351690.8111 | 1187213.7424 | 1024915.3887 | 491543.7657 | 325535.0938 | 161671.4418 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11
|  | Subtotal | CAPEX |  |  | 390813.3365 | 780657.8383 | 1168203.794 | 1553866.4197 | 1938035.1992 | 2321076.0006 | 2703332.7911 | 3085129.3909 | 3466646.1019 | 3847904.034 | 3743074.201 | 3639178.444 | 3537863.7919 | 3438608.0091 | 3340920.7139 | 3244340.7453 | 3148434.0275 | 3052791.3871 | 2957181.9136 | 2861572.4401 | 2766960.2449 | 2675361.378 | 2587839.4108 | 2504484.0352 | 2425386.9163 | 2350641.7356 | 2280344.2357 | 2214592.2658 | 2153485.8274 | 2097127.1221 | 2044380.8753 | 1992847.6666 | 1941314.4579 | 1889781.2492 | 1838248.0405 | 1786714.8318 | 1735181.6231 | 1683648.4144 | 1632115.2057 | 1580581.997 | 1529048.7883 | 1477515.5796 | 1425982.3709 | 1374449.1622 | 1322915.9535 | 1271382.7448 | 1219849.5361 | 1168316.3274 | 1116783.1187 | 1065249.91 | 943802.9954 | 825481.4592 | 710354.0598 | 598491.0682 | 489964.3015 | 384847.1565 | 283214.6449 | 185143.4287 | 90711.8563 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11
|  | Subtotal | O&M |  |  | 280167.4145 | 337267.0387 | 393849.722 | 449958.3275 | 505634.4132 | 560918.2636 | 615848.9185 | 670464.2024 | 655368.6715 | 778894.0383 | 781847.2085 | 784865.3484 | 787949.8874 | 791102.2862 | 794324.0378 | 797616.668 | 800981.736 | 804420.8355 | 807935.5952 | 811527.6796 | 815198.7898 | 818950.6645 | 822785.0804 | 826703.8535 | 830708.8396 | 834801.9354 | 838985.0793 | 843260.2523 | 847629.4792 | 852094.8291 | 856658.4166 | 861322.4031 | 866088.9973 | 870960.4565 | 875939.0879 | 881027.2491 | 886227.3499 | 891541.8529 | 896973.275 | 902524.1883 | 908197.2218 | 913995.062 | 919920.4547 | 925976.206 | 932165.1838 | 938490.3192 | 944954.6075 | 951561.1102 | 958312.9559 | 965213.3423 | 913927.3395 | 861513.0446 | 807945.6352 | 753199.7429 | 697249.4409 | 640068.2323 | 208329.1208 | 140391.6652 | 70959.5855 | 0 | 0 | 0 | 0
|  | Subtotal | O&M - Cost Savings (minus property tax) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Subtotal | O&M - Storm Damage Reductions |  |  | 133638.1253 | 135890.4918 | 136264.6301 | 134777.0167 | 131442.1607 | 126272.6221 | 119279.0284 | 110470.0897 | 99852.6127 | 87431.5124 | 89355.0057 | 91320.8158 | 93329.8737 | 95383.131 | 97481.5599 | 99626.1542 | 101817.9296 | 104057.924 | 106347.1983 | 108686.8367 | 111077.9471 | 113521.6619 | 116019.1385 | 118571.5596 | 121180.1339 | 123846.0968 | 126570.7109 | 129355.2666 | 132201.0824 | 135109.5063 | 138081.9154 | 141119.7175 | 144224.3513 | 147397.2871 | 150640.0274 | 153954.108 | 157341.0983 | 160802.6025 | 164340.2598 | 167955.7455 | 171650.7719 | 175427.0889 | 179286.4848 | 183230.7875 | 187261.8648 | 191381.6258 | 195592.0216 | 199895.0461 | 204292.7371 | 208787.1773 | 213380.4952 | 218074.8661 | 222872.5132 | 227775.7084 | 232786.774 | 237908.0831 | 0 | 0 | 0 | 0 | 0 | 0 | 0
T&D Resilience Projects - Underground (UG) - Detailed Annual Cost Calcs
Phase | Type | Cost Bucket | Cost Category | Notes | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093
1PH | UG | CAPEX | Plant in Service | Handled in Rev Req't Baseline tab
1PH | UG | CAPEX | Depreciation | Handled in Rev Req't Baseline tab
1PH | UG | CAPEX | ADIT | Handled in Rev Req't Baseline tab
1PH | UG | CAPEX | Net Plant in Service | Handled in Rev Req't Baseline tab
1PH | UG | CAPEX | Net Rate Base | Handled in Rev Req't Baseline tab
1PH | UG | CAPEX | Average Rate Base | Handled in Rev Req't Baseline tab
1PH | UG | CAPEX | Capitalized A&G | Handled in Rev Req't Baseline tab
1PH | UG | CAPEX | Pre-tax Return on Rate Base |  |  | 263185.5188 | 524257.5469 | 782088.6526 | 1036992.3441 | 1289260.2213 | 1539163.7101 | 1786955.4647 | 2032870.8012 | 2277025.7593 | 2519404.1378 | 2432798.7554 | 2346965.0618 | 2263263.7533 | 2181263.3839 | 2100558.8238 | 2020769.0839 | 1941535.5514 | 1862520.1871 | 1783532.2236 | 1704544.2602 | 1626380.2003 | 1550705.6077 | 1478399.1543 | 1409534.9391 | 1344188.6914 | 1282437.8064 | 1224361.3822 | 1170040.2568 | 1119557.0468 | 1072996.1864 | 1029419.766 | 986845.4995 | 944271.233 | 901696.9665 | 859122.7 | 816548.4335 | 773974.167 | 731399.9005 | 688825.634 | 646251.3675 | 603677.101 | 561102.8345 | 518528.568 | 475954.3015 | 433380.035 | 390805.7685 | 348231.502 | 305657.2355 | 263082.969 | 220508.7026 | 179860.8079 | 143108.037 | 110336.0826 | 81632.5228 | 57086.8621 | 36790.5744 | 20837.1458 | 9322.1193 | 2343.1397 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10
1PH | UG | CAPEX | Depreciation Expense |  |  | 59685.724 | 120684.5339 | 183025.3177 | 246737.5987 | 311851.5498 | 378398.0079 | 446408.4881 | 515915.1988 | 586951.0572 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 599863.9805 | 538865.1705 | 476524.3868 | 412812.1058 | 347698.1546 | 281151.6965 | 213141.2164 | 143634.5056 | 72598.6473 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | O&M | Outage Restoration - Major/Minor Storm |  |  | 128023.7514 | 128841.9595 | 127621.3413 | 124377.2515 | 119122.917 | 111869.4548 | 102625.8877 | 91399.1587 | 78194.1437 | 63013.6624 | 64399.963 | 65816.7622 | 67264.731 | 68744.555 | 70256.9353 | 71802.5878 | 73382.2448 | 74996.6541 | 76646.5805 | 78332.8053 | 80056.127 | 81817.3618 | 83617.3438 | 85456.9253 | 87336.9777 | 89258.3912 | 91222.0758 | 93228.9615 | 95279.9986 | 97376.1586 | 99518.4341 | 101707.8397 | 103945.4121 | 106232.2112 | 108569.3198 | 110957.8449 | 113398.9175 | 115893.6936 | 118443.3549 | 121049.1087 | 123712.1891 | 126433.8573 | 129215.4021 | 132058.141 | 134963.4201 | 137932.6153 | 140967.1329 | 144068.4098 | 147237.9148 | 150477.1489 | 153787.6462 | 157170.9744 | 160628.7358 | 164162.568 | 167774.1445 | 171465.1757 | 175237.4096 | 179092.6326 | 183032.6705
1PH | UG | O&M | Routine (non-storm) Restoration costs |  |  | 23631.614 | 22097.6764 | 20577.2952 | 19069.6792 | 17574.0449 | 16089.616 | 14615.6232 | 13151.3034 | 11695.8999 | 10248.6614 | 10474.132 | 10704.5629 | 10940.0633 | 11180.7447 | 11426.7211 | 11678.1089 | 11935.0273 | 12197.5979 | 12465.9451 | 12740.1959 | 13020.4802 | 13306.9307 | 13599.6832 | 13898.8763 | 14204.6515 | 14517.1539 | 14836.5312 | 15162.9349 | 15496.5195 | 15837.4429 | 16185.8667 | 16541.9557 | 16905.8788 | 17277.8081 | 17657.9199 | 18046.3941 | 18443.4148 | 18849.1699 | 19263.8517 | 19687.6564 | 20120.7848 | 20563.4421 | 21015.8378 | 21478.1863 | 21950.7064 | 22433.6219 | 22927.1616 | 23431.5591 | 23947.0534 | 24473.8886 | 25012.3142 | 25562.5851 | 26124.9619 | 26699.7111 | 27287.1047 | 27887.421 | 28500.9443 | 29127.9651 | 29768.7803
1PH | UG | O&M | Pole Inspections |  |  | 2388.7571 | 2363.8361 | 2340.1512 | 2317.6885 | 2296.4346 | 2276.3771 | 2257.5038 | 2239.8035 | 2223.2653 | 2207.879 | 2256.4523 | 2306.0943 | 2356.8283 | 2408.6786 | 2461.6695 | 2515.8262 | 2571.1744 | 2627.7402 | 2685.5505 | 2744.6326 | 2805.0145 | 2866.7249 | 2929.7928 | 2994.2483 | 3060.1217 | 3127.4444 | 3196.2482 | 3266.5656 | 3338.4301 | 3411.8755 | 3486.9368 | 3563.6494 | 3642.0497 | 3722.1748 | 3804.0626 | 3887.752 | 3973.2826 | 4060.6948 | 4150.0301 | 4241.3307 | 4334.64 | 4430.0021 | 4527.4621 | 4627.0663 | 4728.8618 | 4832.8967 | 4939.2204 | 5047.8833 | 5158.9367 | 5272.4333 | 5388.4269 | 5506.9723 | 5628.1256 | 5751.9444 | 5878.4872 | 6007.8139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | O&M | Veg Mng - Tree Trimming |  |  | 87844.8177 | 80967.9639 | 74142.7149 | 67365.5329 | 60632.91 | 53941.3662 | 47287.4479 | 40667.7256 | 34078.7925 | 27517.2626 | 28122.6424 | 28741.3406 | 29373.65 | 30019.8703 | 30680.3075 | 31355.2743 | 32045.0903 | 32750.0823 | 33470.5841 | 34206.9369 | 34959.4895 | 35728.5983 | 36514.6275 | 37317.9493 | 38138.9442 | 38978.0009 | 39835.517 | 40711.8983 | 41607.5601 | 42522.9264 | 43458.4308 | 44414.5163 | 45391.6356 | 46390.2516 | 47410.8372 | 48453.8756 | 49519.8608 | 50609.2978 | 51722.7023 | 52860.6018 | 54023.535 | 55212.0528 | 56426.7179 | 57668.1057 | 58936.8041 | 60233.4138 | 61558.5489 | 62912.8369 | 64296.9194 | 65711.4516 | 67157.1035 | 68634.5598 | 70144.5201 | 71687.6995 | 73264.8289 | 74876.6552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | O&M | Veg Mng - Tickets |  |  | 12849.42 | 12114.2577 | 11386.3646 | 10665.3606 | 9950.8698 | 9242.5201 | 8539.9433 | 7842.7743 | 7150.6517 | 6463.217 | 6605.4078 | 6750.7268 | 6899.2428 | 7051.0261 | 7206.1487 | 7364.684 | 7526.707 | 7692.2946 | 7861.525 | 8034.4786 | 8211.2371 | 8391.8843 | 8576.5058 | 8765.1889 | 8958.0231 | 9155.0996 | 9356.5118 | 9562.355 | 9772.7269 | 9987.7268 | 10207.4568 | 10432.0209 | 10661.5253 | 10896.0789 | 11135.7926 | 11380.7801 | 11631.1572 | 11887.0427 | 12148.5576 | 12415.8259 | 12688.9741 | 12968.1315 | 13253.4304 | 13545.0059 | 13842.996 | 14147.5419 | 14458.7878 | 14776.8812 | 15101.9726 | 15434.2159 | 15773.7687 | 16120.7916 | 16475.449 | 16837.9089 | 17208.3429 | 17586.9264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | O&M | Veg Mng - Danger Trees |  |  | 2733.1611 | 2529.2038 | 2326.8417 | 2125.9699 | 1926.4843 | 1728.2818 | 1531.2598 | 1335.3168 | 1140.3519 | 946.2646 | 967.0824 | 988.3582 | 1010.1021 | 1032.3244 | 1055.0355 | 1078.2463 | 1101.9677 | 1126.211 | 1150.9876 | 1176.3094 | 1202.1882 | 1228.6363 | 1255.6663 | 1283.291 | 1311.5234 | 1340.3769 | 1369.8652 | 1400.0022 | 1430.8022 | 1462.2799 | 1494.45 | 1527.328 | 1560.9292 | 1595.2696 | 1630.3655 | 1666.2336 | 1702.8907 | 1740.3543 | 1778.6421 | 1817.7722 | 1857.7632 | 1898.634 | 1940.404 | 1983.0929 | 2026.7209 | 2071.3088 | 2116.8775 | 2163.4489 | 2211.0447 | 2259.6877 | 2309.4008 | 2360.2077 | 2412.1322 | 2465.1991 | 2519.4335 | 2574.8611 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | O&M | Property Taxes |  |  | 48196.2221 | 97452.7611 | 147792.944 | 199240.6109 | 251820.1265 | 305556.3914 | 360474.8541 | 416601.5231 | 416601.5231 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 532586.3864 | 484390.1642 | 435133.6252 | 384793.4423 | 333345.7754 | 280766.2599 | 227029.995 | 172111.5322 | 115984.8633 | 58623.4077 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | O&M | Reduced pole attachment revenue |  |  | 893.3768 | 1785.832 | 2677.8192 | 3569.7911 | 4462.1997 | 5355.4965 | 6250.1327 | 7146.5596 | 8045.2287 | 8946.5919 | 9143.4169 | 9344.5721 | 9550.1526 | 9760.256 | 9974.9816 | 10194.4312 | 10418.7087 | 10647.9203 | 10882.1746 | 11121.5824 | 11366.2572 | 11616.3149 | 11871.8738 | 12133.055 | 12399.9822 | 12672.7818 | 12951.583 | 13236.5179 | 13527.7213 | 13825.3311 | 14129.4884 | 14440.3371 | 14758.0246 | 15082.7011 | 15414.5205 | 15753.64 | 16100.2201 | 16454.4249 | 16816.4223 | 17186.3835 | 17564.484 | 17950.9026 | 18345.8225 | 18749.4306 | 19161.9181 | 19583.4802 | 20014.3168 | 20454.6318 | 20904.6337 | 21364.5356 | 21834.5554 | 22314.9156 | 22805.8438 | 23307.5723 | 23820.3389 | 24344.3864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total Costs impacting revenue requirement |  |  |  | 629432.363 | 993095.5714 | 1353979.4425 | 1712461.8274 | 2068897.758 | 2423621.222 | 2776946.6054 | 3129170.165 | 3423106.6731 | 3830883.7677 | 3746903.9431 | 3663753.5696 | 3582794.6143 | 3503596.9299 | 3425756.7138 | 3348894.3334 | 3272652.5625 | 3196694.7784 | 3120831.6619 | 3045037.2921 | 2970137.085 | 2897798.1498 | 2828900.7384 | 2763520.564 | 2701735.006 | 2643623.146 | 2589265.8052 | 2538745.5831 | 2492146.8963 | 2449556.0187 | 2410036.9205 | 2371609.2374 | 2333272.7791 | 2295029.5527 | 2256881.6091 | 2218831.0446 | 2180880.0015 | 2143030.6694 | 2105285.2858 | 2067646.1376 | 2030115.5621 | 1992695.9477 | 1955389.7357 | 1918199.4209 | 1881127.5531 | 1844176.738 | 1807349.6388 | 1770648.9773 | 1734077.5351 | 1697638.1551 | 1555378.1682 | 1414777.8392 | 1275873.6803 | 1138703.0075 | 1003303.9573 | 869715.5056 | 609828.2483 | 477162.0859 | 346366.6454 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10
|  | Subtotal | CAPEX |  |  | 322871.2428 | 644942.0808 | 965113.9703 | 1283729.9428 | 1601111.7712 | 1917561.7181 | 2233363.9528 | 2548786 | 2863976.8165 | 3178953.8423 | 3092348.4599 | 3006514.7663 | 2922813.4578 | 2840813.0884 | 2760108.5283 | 2680318.7884 | 2601085.2559 | 2522069.8916 | 2443081.9281 | 2364093.9647 | 2285929.9048 | 2210255.3122 | 2137948.8588 | 2069084.6436 | 2003738.3959 | 1941987.5109 | 1883911.0866 | 1829589.9613 | 1779106.7513 | 1732545.8909 | 1688969.4705 | 1646395.204 | 1603820.9375 | 1561246.671 | 1518672.4045 | 1476098.138 | 1433523.8715 | 1390949.605 | 1348375.3385 | 1305801.072 | 1263226.8055 | 1220652.539 | 1178078.2725 | 1135504.006 | 1092929.7395 | 1050355.473 | 1007781.2065 | 965206.94 | 922632.6735 | 880058.407 | 779724.7883 | 681973.2075 | 586860.4694 | 494444.6286 | 404785.0167 | 317942.2709 | 233978.3622 | 152956.6249 | 74941.7869 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10
|  | Subtotal | O&M |  |  | 306561.1202 | 348153.4906 | 388865.4722 | 428731.8846 | 467785.9869 | 506059.504 | 543582.6525 | 580384.165 | 559129.8566 | 651929.9254 | 654555.4832 | 657238.8034 | 659981.1565 | 662783.8415 | 665648.1855 | 668575.5451 | 671567.3066 | 674624.8868 | 677749.7338 | 680943.3275 | 684207.1802 | 687542.8376 | 690951.8796 | 694435.9204 | 697996.6102 | 701635.6351 | 705354.7185 | 709155.6219 | 713040.145 | 717010.1277 | 721067.45 | 725214.0334 | 729451.8417 | 733782.8817 | 738209.2046 | 742732.9066 | 747356.13 | 752081.0644 | 756909.9473 | 761845.0657 | 766888.7566 | 772043.4087 | 777311.4632 | 782695.4149 | 788197.8136 | 793821.265 | 799568.4323 | 805442.0373 | 811444.8616 | 817579.7481 | 775653.3799 | 732804.6316 | 689013.2109 | 644258.3789 | 598518.9406 | 551773.2347 | 375849.8861 | 324205.461 | 271424.8585 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Subtotal | O&M - Cost Savings (minus property tax) |  |  | 106709.5327 | 99761.0936 | 92873.8916 | 86044.343 | 79268.8984 | 72544.0417 | 65866.2875 | 59232.1798 | 52638.29 | 46081.2151 | 47095.0019 | 48131.0919 | 49189.9759 | 50272.1554 | 51378.1428 | 52508.4619 | 53663.6481 | 54844.2484 | 56050.8218 | 57283.9399 | 58544.1866 | 59832.1587 | 61148.4662 | 62493.7324 | 63868.5946 | 65273.7036 | 66709.7251 | 68177.3391 | 69677.2405 | 71210.1398 | 72776.7629 | 74377.8517 | 76014.1644 | 77686.476 | 79395.5785 | 81142.2812 | 82927.4114 | 84751.8145 | 86616.3544 | 88521.9142 | 90469.3963 | 92459.723 | 94493.8369 | 96572.7013 | 98697.3008 | 100868.6414 | 103087.7515 | 105355.682 | 107673.507 | 110042.3242 | 112463.2553 | 114937.4469 | 117466.0708 | 120050.3243 | 122691.4315 | 125390.643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Subtotal | O&M - Storm Damage Reductions |  |  | 128023.7514 | 128841.9595 | 127621.3413 | 124377.2515 | 119122.917 | 111869.4548 | 102625.8877 | 91399.1587 | 78194.1437 | 63013.6624 | 64399.963 | 65816.7622 | 67264.731 | 68744.555 | 70256.9353 | 71802.5878 | 73382.2448 | 74996.6541 | 76646.5805 | 78332.8053 | 80056.127 | 81817.3618 | 83617.3438 | 85456.9253 | 87336.9777 | 89258.3912 | 91222.0758 | 93228.9615 | 95279.9986 | 97376.1586 | 99518.4341 | 101707.8397 | 103945.4121 | 106232.2112 | 108569.3198 | 110957.8449 | 113398.9175 | 115893.6936 | 118443.3549 | 121049.1087 | 123712.1891 | 126433.8573 | 129215.4021 | 132058.141 | 134963.4201 | 137932.6153 | 140967.1329 | 144068.4098 | 147237.9148 | 150477.1489 | 153787.6462 | 157170.9744 | 160628.7358 | 164162.568 | 167774.1445 | 171465.1757 | 175237.4096 | 179092.6326 | 183032.6705 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rollup costs
[6 empty] | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090
|  |  | Pre-tax Return on Rate Base |  |  | 670219.8079 | 1335057.4681 | 1991641.8993 | 2640771.4712 | 3283188.7629 | 3919584.9789 | 4550603.5202 | 5176843.6353 | 5798600.8271 | 6415833.8385 | 6195287.347 | 5976706.0136 | 5763554.9437 | 5554735.4309 | 5349215.7845 | 5146025.7898 | 4944252.2152 | 4743034.2206 | 4541886.0042 | 4340737.7877 | 4141687.6978 | 3948977.2055 | 3764843.9084 | 3589476.5049 | 3423067.8446 | 3265815.0198 | 3117919.4589 | 2979587.0218 | 2851028.0972 | 2732457.7023 | 2621487.3864 | 2513069.1237 | 2404650.861 | 2296232.5983 | 2187814.3357 | 2079396.073 | 1970977.8103 | 1862559.5476 | 1754141.2849 | 1645723.0222 | 1537304.7595 | 1428886.4968 | 1320468.2341 | 1212049.9715 | 1103631.7088 | 995213.4461 | 886795.1834 | 778376.9207 | 669958.658 | 561540.3953 | 458027.7693 | 364434.3408 | 280978.3321 | 207882.7665 | 145375.5736 | 93689.6977 | 53063.2077 | 23739.4102 | 5966.9644 | 1.3969e-11 | 1.3969e-11 | 1.3969e-11 | 1.3969e-11
|  |  | Depreciation Expense |  |  | 151993.752 | 307331.3665 | 466086.4086 | 628334.0616 | 794151.163 | 963616.2405 | 1136809.5498 | 1313813.1119 | 1494710.7524 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1679588.1409 | 1527594.3889 | 1372256.7744 | 1213501.7323 | 1051254.0793 | 885436.978 | 715971.9004 | 542778.5911 | 365775.029 | 184877.3886 | 0 | 0 | 0 | 0
|  |  | Outage Restoration - Major/Minor Storm |  |  | 313612.0053 | 317558.1588 | 316857.1205 | 311547.1264 | 301661.5529 | 287228.9594 | 268273.1276 | 244813.0966 | 216863.1949 | 184433.0679 | 188490.5954 | 192637.3885 | 196875.411 | 201206.6701 | 205633.2168 | 210157.1476 | 214780.6049 | 219505.7782 | 224334.9053 | 229270.2732 | 234314.2192 | 239469.132 | 244737.4529 | 250121.6769 | 255624.3538 | 261248.0896 | 266995.5475 | 272869.4496 | 278872.5775 | 285007.7742 | 291277.9452 | 297686.06 | 304235.1533 | 310928.3267 | 317768.7499 | 324759.6624 | 331904.375 | 339206.2712 | 346668.8092 | 354295.523 | 362090.0245 | 370056.005 | 378197.2371 | 386517.5764 | 395020.963 | 403711.4242 | 412593.0756 | 421670.1232 | 430946.8659 | 440427.697 | 450117.1063 | 460019.6826 | 470140.1157 | 480483.1982 | 491053.8286 | 501857.0128 | 175237.4096 | 179092.6326 | 183032.6705 | 0 | 0 | 0 | 0
|  |  | Routine (non-storm) Restoration costs |  |  | 119647.1049 | 112915.1993 | 106250.863 | 99650.6152 | 93111.0131 | 86628.6497 | 80200.1524 | 73822.181 | 67491.4262 | 61204.6076 | 62551.1089 | 63927.2333 | 65333.6325 | 66770.9724 | 68239.9338 | 69741.2123 | 71275.519 | 72843.5804 | 74446.1392 | 76083.9542 | 77757.8012 | 79468.4729 | 81216.7793 | 83003.5484 | 84829.6265 | 86695.8783 | 88603.1876 | 90552.4577 | 92544.6118 | 94580.5932 | 96661.3663 | 98787.9163 | 100961.2505 | 103182.398 | 105452.4108 | 107772.3638 | 110143.3558 | 112566.5096 | 115042.9728 | 117573.9182 | 120160.5444 | 122804.0764 | 125505.7661 | 128266.893 | 131088.7646 | 133972.7174 | 136920.1172 | 139932.3598 | 143010.8717 | 146157.1109 | 149372.5673 | 152658.7638 | 156017.2566 | 159449.6363 | 162957.5282 | 166542.5939 | 28500.9443 | 29127.9651 | 29768.7803 | 0 | 0 | 0 | 0
|  |  | Pole Inspections |  |  | 2388.7571 | 2363.8361 | 2340.1512 | 2317.6885 | 2296.4346 | 2276.3771 | 2257.5038 | 2239.8035 | 2223.2653 | 2207.879 | 2256.4523 | 2306.0943 | 2356.8283 | 2408.6786 | 2461.6695 | 2515.8262 | 2571.1744 | 2627.7402 | 2685.5505 | 2744.6326 | 2805.0145 | 2866.7249 | 2929.7928 | 2994.2483 | 3060.1217 | 3127.4444 | 3196.2482 | 3266.5656 | 3338.4301 | 3411.8755 | 3486.9368 | 3563.6494 | 3642.0497 | 3722.1748 | 3804.0626 | 3887.752 | 3973.2826 | 4060.6948 | 4150.0301 | 4241.3307 | 4334.64 | 4430.0021 | 4527.4621 | 4627.0663 | 4728.8618 | 4832.8967 | 4939.2204 | 5047.8833 | 5158.9367 | 5272.4333 | 5388.4269 | 5506.9723 | 5628.1256 | 5751.9444 | 5878.4872 | 6007.8139 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Veg Mng - Tree Trimming |  |  | 87844.8177 | 80967.9639 | 74142.7149 | 67365.5329 | 60632.91 | 53941.3662 | 47287.4479 | 40667.7256 | 34078.7925 | 27517.2626 | 28122.6424 | 28741.3406 | 29373.65 | 30019.8703 | 30680.3075 | 31355.2743 | 32045.0903 | 32750.0823 | 33470.5841 | 34206.9369 | 34959.4895 | 35728.5983 | 36514.6275 | 37317.9493 | 38138.9442 | 38978.0009 | 39835.517 | 40711.8983 | 41607.5601 | 42522.9264 | 43458.4308 | 44414.5163 | 45391.6356 | 46390.2516 | 47410.8372 | 48453.8756 | 49519.8608 | 50609.2978 | 51722.7023 | 52860.6018 | 54023.535 | 55212.0528 | 56426.7179 | 57668.1057 | 58936.8041 | 60233.4138 | 61558.5489 | 62912.8369 | 64296.9194 | 65711.4516 | 67157.1035 | 68634.5598 | 70144.5201 | 71687.6995 | 73264.8289 | 74876.6552 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Veg Mng - Tickets |  |  | 12849.42 | 12114.2577 | 11386.3646 | 10665.3606 | 9950.8698 | 9242.5201 | 8539.9433 | 7842.7743 | 7150.6517 | 6463.217 | 6605.4078 | 6750.7268 | 6899.2428 | 7051.0261 | 7206.1487 | 7364.684 | 7526.707 | 7692.2946 | 7861.525 | 8034.4786 | 8211.2371 | 8391.8843 | 8576.5058 | 8765.1889 | 8958.0231 | 9155.0996 | 9356.5118 | 9562.355 | 9772.7269 | 9987.7268 | 10207.4568 | 10432.0209 | 10661.5253 | 10896.0789 | 11135.7926 | 11380.7801 | 11631.1572 | 11887.0427 | 12148.5576 | 12415.8259 | 12688.9741 | 12968.1315 | 13253.4304 | 13545.0059 | 13842.996 | 14147.5419 | 14458.7878 | 14776.8812 | 15101.9726 | 15434.2159 | 15773.7687 | 16120.7916 | 16475.449 | 16837.9089 | 17208.3429 | 17586.9264 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Veg Mng - Danger Trees |  |  | 2733.1611 | 2529.2038 | 2326.8417 | 2125.9699 | 1926.4843 | 1728.2818 | 1531.2598 | 1335.3168 | 1140.3519 | 946.2646 | 967.0824 | 988.3582 | 1010.1021 | 1032.3244 | 1055.0355 | 1078.2463 | 1101.9677 | 1126.211 | 1150.9876 | 1176.3094 | 1202.1882 | 1228.6363 | 1255.6663 | 1283.291 | 1311.5234 | 1340.3769 | 1369.8652 | 1400.0022 | 1430.8022 | 1462.2799 | 1494.45 | 1527.328 | 1560.9292 | 1595.2696 | 1630.3655 | 1666.2336 | 1702.8907 | 1740.3543 | 1778.6421 | 1817.7722 | 1857.7632 | 1898.634 | 1940.404 | 1983.0929 | 2026.7209 | 2071.3088 | 2116.8775 | 2163.4489 | 2211.0447 | 2259.6877 | 2309.4008 | 2360.2077 | 2412.1322 | 2465.1991 | 2519.4335 | 2574.8611 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Property Taxes |  |  | 122734.9547 | 248170.0785 | 376364.775 | 507379.7547 | 641277.0641 | 778120.1142 | 917973.7115 | 1060904.0879 | 1060904.0879 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1356267.4238 | 1233532.4691 | 1108097.3453 | 979902.6489 | 848887.6691 | 714990.3597 | 578147.3096 | 438293.7123 | 295363.3359 | 149288.4913 | 0 | 0 | 0 | 0
|  |  | Reduced pole attachment revenue |  |  | 893.3768 | 1785.832 | 2677.8192 | 3569.7911 | 4462.1997 | 5355.4965 | 6250.1327 | 7146.5596 | 8045.2287 | 8946.5919 | 9143.4169 | 9344.5721 | 9550.1526 | 9760.256 | 9974.9816 | 10194.4312 | 10418.7087 | 10647.9203 | 10882.1746 | 11121.5824 | 11366.2572 | 11616.3149 | 11871.8738 | 12133.055 | 12399.9822 | 12672.7818 | 12951.583 | 13236.5179 | 13527.7213 | 13825.3311 | 14129.4884 | 14440.3371 | 14758.0246 | 15082.7011 | 15414.5205 | 15753.64 | 16100.2201 | 16454.4249 | 16816.4223 | 17186.3835 | 17564.484 | 17950.9026 | 18345.8225 | 18749.4306 | 19161.9181 | 19583.4802 | 20014.3168 | 20454.6318 | 20904.6337 | 21364.5356 | 21834.5554 | 22314.9156 | 22805.8438 | 23307.5723 | 23820.3389 | 24344.3864 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Costs_Mitigation
[5 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63
T&D Resilience Projects - Overhead (OH) Spacer Cable - Detailed Annual Cost Calcs
Phase | Type | Cost Bucket | Cost Category | Notes | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090
1PH | OH | CAPEX | Plant in Service |  | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 10031291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | OH | CAPEX | Cumulative Depreciation |  | 0 | -200625.82 | -401251.64 | -601877.46 | -802503.28 | -1003129.1 | -1203754.92 | -1404380.74 | -1605006.56 | -1805632.38 | -2006258.2 | -2206884.02 | -2407509.84 | -2608135.66 | -2808761.48 | -3009387.3 | -3210013.12 | -3410638.94 | -3611264.76 | -3811890.58 | -4012516.4 | -4213142.22 | -4413768.04 | -4614393.86 | -4815019.68 | -5015645.5 | -5216271.32 | -5416897.14 | -5617522.96 | -5818148.78 | -6018774.6 | -6219400.42 | -6420026.24 | -6620652.06 | -6821277.88 | -7021903.7 | -7222529.52 | -7423155.34 | -7623781.16 | -7824406.98 | -8025032.8 | -8225658.62 | -8426284.44 | -8626910.26 | -8827536.08 | -9028161.9 | -9228787.72 | -9429413.54 | -9630039.36 | -9830665.18 | -10031291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | OH | CAPEX | Net Plant (b.o.y.) |  | 0 | 10031291 | 9830665.18 | 9630039.36 | 9429413.54 | 9228787.72 | 9028161.9 | 8827536.08 | 8626910.26 | 8426284.44 | 8225658.62 | 8025032.8 | 7824406.98 | 7623781.16 | 7423155.34 | 7222529.52 | 7021903.7 | 6821277.88 | 6620652.06 | 6420026.24 | 6219400.42 | 6018774.6 | 5818148.78 | 5617522.96 | 5416897.14 | 5216271.32 | 5015645.5 | 4815019.68 | 4614393.86 | 4413768.04 | 4213142.22 | 4012516.4 | 3811890.58 | 3611264.76 | 3410638.94 | 3210013.12 | 3009387.3 | 2808761.48 | 2608135.66 | 2407509.84 | 2206884.02 | 2006258.2 | 1805632.38 | 1605006.56 | 1404380.74 | 1203754.92 | 1003129.1 | 802503.28 | 601877.46 | 401251.64 | 200625.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | OH | CAPEX | Net Plant (e.o.y.) |  | 10031291 | 9830665.18 | 9630039.36 | 9429413.54 | 9228787.72 | 9028161.9 | 8827536.08 | 8626910.26 | 8426284.44 | 8225658.62 | 8025032.8 | 7824406.98 | 7623781.16 | 7423155.34 | 7222529.52 | 7021903.7 | 6821277.88 | 6620652.06 | 6420026.24 | 6219400.42 | 6018774.6 | 5818148.78 | 5617522.96 | 5416897.14 | 5216271.32 | 5015645.5 | 4815019.68 | 4614393.86 | 4413768.04 | 4213142.22 | 4012516.4 | 3811890.58 | 3611264.76 | 3410638.94 | 3210013.12 | 3009387.3 | 2808761.48 | 2608135.66 | 2407509.84 | 2206884.02 | 2006258.2 | 1805632.38 | 1605006.56 | 1404380.74 | 1203754.92 | 1003129.1 | 802503.28 | 601877.46 | 401251.64 | 200625.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | OH | CAPEX | MACRS depreciation |  | 0 | 376173.4125 | 724158.8973 | 669789.3001 | 619632.8451 | 573087.6548 | 530153.7294 | 490329.5041 | 453614.979 | 447596.2044 | 447495.8915 | 447596.2044 | 447495.8915 | 447596.2044 | 447495.8915 | 447596.2044 | 447495.8915 | 447596.2044 | 447495.8915 | 447596.2044 | 447495.8915 | 223798.1022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | OH | CAPEX | ADIT (b.o.y.) |  | 0 | 0 | -48653.0153 | -193750.2076 | -323778.8661 | -439906.6631 | -543134.4607 | -634463.1207 | -714754.4968 | -784870.4422 | -853318.2842 | -921738.3246 | -990186.1666 | -1058606.2069 | -1127054.049 | -1195474.0893 | -1263921.9313 | -1332341.9716 | -1400789.8137 | -1469209.854 | -1537657.696 | -1606077.7364 | -1612499.9344 | -1556896.4884 | -1501293.0424 | -1445689.5963 | -1390086.1503 | -1334482.7043 | -1278879.2583 | -1223275.8123 | -1167672.3663 | -1112068.9203 | -1056465.4742 | -1000862.0282 | -945258.5822 | -889655.1362 | -834051.6902 | -778448.2442 | -722844.7982 | -667241.3522 | -611637.9061 | -556034.4601 | -500431.0141 | -444827.5681 | -389224.1221 | -333620.6761 | -278017.2301 | -222413.7841 | -166810.338 | -111206.892 | -55603.446 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10
1PH | OH | CAPEX | ADIT (e.o.y.) |  |  | -48653.0153 | -193750.2076 | -323778.8661 | -439906.6631 | -543134.4607 | -634463.1207 | -714754.4968 | -784870.4422 | -853318.2842 | -921738.3246 | -990186.1666 | -1058606.2069 | -1127054.049 | -1195474.0893 | -1263921.9313 | -1332341.9716 | -1400789.8137 | -1469209.854 | -1537657.696 | -1606077.7364 | -1612499.9344 | -1556896.4884 | -1501293.0424 | -1445689.5963 | -1390086.1503 | -1334482.7043 | -1278879.2583 | -1223275.8123 | -1167672.3663 | -1112068.9203 | -1056465.4742 | -1000862.0282 | -945258.5822 | -889655.1362 | -834051.6902 | -778448.2442 | -722844.7982 | -667241.3522 | -611637.9061 | -556034.4601 | -500431.0141 | -444827.5681 | -389224.1221 | -333620.6761 | -278017.2301 | -222413.7841 | -166810.338 | -111206.892 | -55603.446 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10
1PH | OH | CAPEX | Net Rate Base |  |  | 9906651.5824 | 9609150.6586 | 9270961.9131 | 8947257.8654 | 8636954.2481 | 8339050.1993 | 8052614.3612 | 7776784.8805 | 7506877.1668 | 7237817.4056 | 6968757.6444 | 6699697.8832 | 6430638.1221 | 6161578.3609 | 5892518.5997 | 5623458.8385 | 5354399.0773 | 5085339.3162 | 4816279.555 | 4547219.7938 | 4309172.8546 | 4133137.6586 | 3988115.2846 | 3843092.9107 | 3698070.5367 | 3553048.1627 | 3408025.7887 | 3263003.4147 | 3117981.0407 | 2972958.6667 | 2827936.2927 | 2682913.9188 | 2537891.5448 | 2392869.1708 | 2247846.7968 | 2102824.4228 | 1957802.0488 | 1812779.6748 | 1667757.3009 | 1522734.9269 | 1377712.5529 | 1232690.1789 | 1087667.8049 | 942645.4309 | 797623.0569 | 652600.6829 | 507578.309 | 362555.935 | 217533.561 | 72511.187 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10 | 9.4587e-10
1PH | OH | CAPEX | Pre-tax Return on Rate Base |  |  | 884663.9863 | 858097.1538 | 827896.8988 | 798990.1274 | 771280.0144 | 744677.1828 | 719098.4625 | 694466.8898 | 670364.131 | 646337.0943 | 622310.0576 | 598283.021 | 574255.9843 | 550228.9476 | 526201.911 | 502174.8743 | 478147.8376 | 454120.8009 | 430093.7643 | 406066.7276 | 384809.1359 | 369089.1929 | 356138.6949 | 343188.1969 | 330237.6989 | 317287.2009 | 304336.7029 | 291386.2049 | 278435.7069 | 265485.2089 | 252534.7109 | 239584.2129 | 226633.7149 | 213683.217 | 200732.719 | 187782.221 | 174831.723 | 161881.225 | 148930.727 | 135980.229 | 123029.731 | 110079.233 | 97128.735 | 84178.237 | 71227.739 | 58277.241 | 45326.743 | 32376.245 | 19425.747 | 6475.249 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11
1PH | OH | CAPEX | Depreciation Expense |  |  | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 200625.82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | OH | O&M | Outage Restoration - Major/Minor Storm |  |  | 5708.8053 | 6411.1545 | 7141.6439 | 7901.1719 | 8690.6626 | 9511.0666 | 10363.3622 | 11248.5554 | 12167.6813 | 13121.8044 | 13410.4841 | 13705.5147 | 14007.036 | 14315.1908 | 14630.125 | 14951.9878 | 15280.9315 | 15617.112 | 15960.6885 | 16311.8236 | 16670.6837 | 17037.4388 | 17412.2624 | 17795.3322 | 18186.8295 | 18586.9398 | 18995.8524 | 19413.7612 | 19840.8639 | 20277.3629 | 20723.4649 | 21179.3812 | 21645.3275 | 22121.5247 | 22608.1983 | 23105.5787 | 23613.9014 | 24133.4072 | 24664.3422 | 25206.9577 | 25761.5108 | 26328.264 | 26907.4858 | 27499.4505 | 28104.4384 | 28722.7361 | 29354.6363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | OH | O&M | Routine (non-storm) Restoration costs |  |  | 2336.4839 | 2387.8865 | 2440.42 | 2494.1093 | 2548.9797 | 2605.0572 | 2662.3685 | 2720.9406 | 2780.8013 | 2841.9789 | 2904.5024 | 2968.4015 | 3033.7063 | 3100.4479 | 3168.6577 | 3238.3682 | 3309.6123 | 3382.4237 | 3456.8371 | 3532.8875 | 3610.611 | 3690.0445 | 3771.2254 | 3854.1924 | 3938.9846 | 4025.6423 | 4114.2064 | 4204.719 | 4297.2228 | 4391.7617 | 4488.3804 | 4587.1248 | 4688.0415 | 4791.1785 | 4896.5844 | 5004.3092 | 5114.404 | 5226.9209 | 5341.9132 | 5459.4353 | 5579.5429 | 5702.2928 | 5827.7433 | 5955.9536 | 6086.9846 | 6220.8982 | 6357.758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | OH | O&M | Pole Inspections | Not included as no change
1PH | OH | O&M | Veg Mng - Tree Trimming | Not included as no change
1PH | OH | O&M | Veg Mng - Tickets | Not included as no change
1PH | OH | O&M | Veg Mng - Danger Trees | Not included as no change
1PH | OH | O&M | Property Taxes |  | 0 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 162005.3496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | OH | O&M | Reduced pole attachment revenue | Not included as no change
|  | Total Costs impacting revenue requirement |  |  |  | 1255340.4452 | 1229527.3645 | 1200110.1324 | 1172016.5782 | 1145150.8262 | 1119424.4763 | 1094755.3628 | 1071067.5555 | 1047943.7832 | 1024932.0472 | 1001256.2138 | 977588.1068 | 953927.8963 | 930275.756 | 906631.8633 | 882996.3999 | 859369.551 | 835751.5063 | 812142.4595 | 788542.6083 | 767721.6003 | 752447.8458 | 739953.3524 | 727468.8912 | 714994.6827 | 702530.9526 | 690077.9314 | 677635.8547 | 665204.9633 | 652785.5032 | 640377.726 | 627981.8886 | 615598.2537 | 603227.0898 | 590868.6713 | 578523.2785 | 566191.198 | 553872.7228 | 541568.152 | 529277.7916 | 517001.9543 | 504740.9594 | 492495.1337 | 480264.8107 | 468050.3316 | 455852.0449 | 443670.3069 | 395007.4146 | 382056.9166 | 369106.4186 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11
|  | Subtotal | CAPEX |  |  | 1085289.8063 | 1058722.9738 | 1028522.7188 | 999615.9474 | 971905.8344 | 945303.0028 | 919724.2825 | 895092.7098 | 870989.951 | 846962.9143 | 822935.8776 | 798908.841 | 774881.8043 | 750854.7676 | 726827.731 | 702800.6943 | 678773.6576 | 654746.6209 | 630719.5843 | 606692.5476 | 585434.9559 | 569715.0129 | 556764.5149 | 543814.0169 | 530863.5189 | 517913.0209 | 504962.5229 | 492012.0249 | 479061.5269 | 466111.0289 | 453160.5309 | 440210.0329 | 427259.5349 | 414309.037 | 401358.539 | 388408.041 | 375457.543 | 362507.045 | 349556.547 | 336606.049 | 323655.551 | 310705.053 | 297754.555 | 284804.057 | 271853.559 | 258903.061 | 245952.563 | 233002.065 | 220051.567 | 207101.069 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11 | 8.4467e-11
|  | Subtotal | O&M |  |  | 170050.6389 | 170804.3906 | 171587.4136 | 172400.6308 | 173244.9919 | 174121.4735 | 175031.0803 | 175974.8456 | 176953.8322 | 177969.1329 | 178320.3361 | 178679.2659 | 179046.092 | 179420.9883 | 179804.1324 | 180195.7056 | 180595.8934 | 181004.8854 | 181422.8752 | 181850.0608 | 182286.6444 | 182732.8329 | 183188.8375 | 183654.8742 | 184131.1638 | 184617.9317 | 185115.4085 | 185623.8298 | 186143.4364 | 186674.4743 | 187217.195 | 187771.8556 | 188338.7187 | 188918.0529 | 189510.1323 | 190115.2375 | 190733.6551 | 191365.6778 | 192011.605 | 192671.7426 | 193346.4033 | 194035.9065 | 194740.5787 | 195460.7538 | 196196.7726 | 196948.984 | 197717.7439 | 162005.3496 | 162005.3496 | 162005.3496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Subtotal | O&M - Cost Savings (minus property tax) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Subtotal | O&M - Storm Damage Reductions |  |  | 5708.8053 | 6411.1545 | 7141.6439 | 7901.1719 | 8690.6626 | 9511.0666 | 10363.3622 | 11248.5554 | 12167.6813 | 13121.8044 | 13410.4841 | 13705.5147 | 14007.036 | 14315.1908 | 14630.125 | 14951.9878 | 15280.9315 | 15617.112 | 15960.6885 | 16311.8236 | 16670.6837 | 17037.4388 | 17412.2624 | 17795.3322 | 18186.8295 | 18586.9398 | 18995.8524 | 19413.7612 | 19840.8639 | 20277.3629 | 20723.4649 | 21179.3812 | 21645.3275 | 22121.5247 | 22608.1983 | 23105.5787 | 23613.9014 | 24133.4072 | 24664.3422 | 25206.9577 | 25761.5108 | 26328.264 | 26907.4858 | 27499.4505 | 28104.4384 | 28722.7361 | 29354.6363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Phase | Type | Cost Bucket | Cost Category | Notes | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090
Phase | Type
3PH | OH | CAPEX | Plant in Service |  | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 36122723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3PH | OH | CAPEX | Cumulative Depreciation |  | 0 | -722454.46 | -1444908.92 | -2167363.38 | -2889817.84 | -3612272.3 | -4334726.76 | -5057181.22 | -5779635.68 | -6502090.14 | -7224544.6 | -7946999.06 | -8669453.52 | -9391907.98 | -10114362.44 | -10836816.9 | -11559271.36 | -12281725.82 | -13004180.28 | -13726634.74 | -14449089.2 | -15171543.66 | -15893998.12 | -16616452.58 | -17338907.04 | -18061361.5 | -18783815.96 | -19506270.42 | -20228724.88 | -20951179.34 | -21673633.8 | -22396088.26 | -23118542.72 | -23840997.18 | -24563451.64 | -25285906.1 | -26008360.56 | -26730815.02 | -27453269.48 | -28175723.94 | -28898178.4 | -29620632.86 | -30343087.32 | -31065541.78 | -31787996.24 | -32510450.7 | -33232905.16 | -33955359.62 | -34677814.08 | -35400268.54 | -36122723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3PH | OH | CAPEX | Net Plant (b.o.y.) |  | 0 | 36122723 | 35400268.54 | 34677814.08 | 33955359.62 | 33232905.16 | 32510450.7 | 31787996.24 | 31065541.78 | 30343087.32 | 29620632.86 | 28898178.4 | 28175723.94 | 27453269.48 | 26730815.02 | 26008360.56 | 25285906.1 | 24563451.64 | 23840997.18 | 23118542.72 | 22396088.26 | 21673633.8 | 20951179.34 | 20228724.88 | 19506270.42 | 18783815.96 | 18061361.5 | 17338907.04 | 16616452.58 | 15893998.12 | 15171543.66 | 14449089.2 | 13726634.74 | 13004180.28 | 12281725.82 | 11559271.36 | 10836816.9 | 10114362.44 | 9391907.98 | 8669453.52 | 7946999.06 | 7224544.6 | 6502090.14 | 5779635.68 | 5057181.22 | 4334726.76 | 3612272.3 | 2889817.84 | 2167363.38 | 1444908.92 | 722454.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3PH | OH | CAPEX | Net Plant (e.o.y.) |  | 36122723 | 35400268.54 | 34677814.08 | 33955359.62 | 33232905.16 | 32510450.7 | 31787996.24 | 31065541.78 | 30343087.32 | 29620632.86 | 28898178.4 | 28175723.94 | 27453269.48 | 26730815.02 | 26008360.56 | 25285906.1 | 24563451.64 | 23840997.18 | 23118542.72 | 22396088.26 | 21673633.8 | 20951179.34 | 20228724.88 | 19506270.42 | 18783815.96 | 18061361.5 | 17338907.04 | 16616452.58 | 15893998.12 | 15171543.66 | 14449089.2 | 13726634.74 | 13004180.28 | 12281725.82 | 11559271.36 | 10836816.9 | 10114362.44 | 9391907.98 | 8669453.52 | 7946999.06 | 7224544.6 | 6502090.14 | 5779635.68 | 5057181.22 | 4334726.76 | 3612272.3 | 2889817.84 | 2167363.38 | 1444908.92 | 722454.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3PH | OH | CAPEX | MACRS depreciation |  | 0 | 1354602.1125 | 2607699.3734 | 2411914.2147 | 2231300.5997 | 2063691.165 | 1909085.9106 | 1765678.7002 | 1633469.5341 | 1611795.9003 | 1611434.673 | 1611795.9003 | 1611434.673 | 1611795.9003 | 1611434.673 | 1611795.9003 | 1611434.673 | 1611795.9003 | 1611434.673 | 1611795.9003 | 1611434.673 | 805897.9501 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3PH | OH | CAPEX | ADIT (b.o.y.) |  | 0 | 0 | -175199.7219 | -697695.3496 | -1165929.1206 | -1584105.8283 | -1955829.5811 | -2284704.4876 | -2573834.0858 | -2826321.9135 | -3072802.8937 | -3319183.7597 | -3565664.7399 | -3812045.606 | -4058526.5861 | -4304907.4522 | -4551388.4323 | -4797769.2984 | -5044250.2785 | -5290631.1446 | -5537112.1248 | -5783492.9908 | -5806619.3541 | -5606391.1005 | -5406162.8469 | -5205934.5933 | -5005706.3397 | -4805478.0861 | -4605249.8325 | -4405021.579 | -4204793.3254 | -4004565.0718 | -3804336.8182 | -3604108.5646 | -3403880.311 | -3203652.0574 | -3003423.8038 | -2803195.5502 | -2602967.2967 | -2402739.0431 | -2202510.7895 | -2002282.5359 | -1802054.2823 | -1601826.0287 | -1401597.7751 | -1201369.5215 | -1001141.2679 | -800913.0144 | -600684.7608 | -400456.5072 | -200228.2536 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09
3PH | OH | CAPEX | ADIT (e.o.y.) |  |  | -175199.7219 | -697695.3496 | -1165929.1206 | -1584105.8283 | -1955829.5811 | -2284704.4876 | -2573834.0858 | -2826321.9135 | -3072802.8937 | -3319183.7597 | -3565664.7399 | -3812045.606 | -4058526.5861 | -4304907.4522 | -4551388.4323 | -4797769.2984 | -5044250.2785 | -5290631.1446 | -5537112.1248 | -5783492.9908 | -5806619.3541 | -5606391.1005 | -5406162.8469 | -5205934.5933 | -5005706.3397 | -4805478.0861 | -4605249.8325 | -4405021.579 | -4204793.3254 | -4004565.0718 | -3804336.8182 | -3604108.5646 | -3403880.311 | -3203652.0574 | -3003423.8038 | -2803195.5502 | -2602967.2967 | -2402739.0431 | -2202510.7895 | -2002282.5359 | -1802054.2823 | -1601826.0287 | -1401597.7751 | -1201369.5215 | -1001141.2679 | -800913.0144 | -600684.7608 | -400456.5072 | -200228.2536 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09
3PH | OH | CAPEX | Net Rate Base |  |  | 35673895.9091 | 34602593.7742 | 33384774.6149 | 32219114.9155 | 31101710.2253 | 30028956.4357 | 28997499.7233 | 28004236.5504 | 27032297.6864 | 26063412.3033 | 25094526.9202 | 24125641.5371 | 23156756.154 | 22187870.7709 | 21218985.3878 | 20250100.0046 | 19281214.6215 | 18312329.2384 | 17343443.8553 | 16374558.4722 | 15517350.3976 | 14883446.8827 | 14361220.6763 | 13838994.4699 | 13316768.2635 | 12794542.0571 | 12272315.8507 | 11750089.6442 | 11227863.4378 | 10705637.2314 | 10183411.025 | 9661184.8186 | 9138958.6122 | 8616732.4058 | 8094506.1994 | 7572279.993 | 7050053.7865 | 6527827.5801 | 6005601.3737 | 5483375.1673 | 4961148.9609 | 4438922.7545 | 3916696.5481 | 3394470.3417 | 2872244.1353 | 2350017.9288 | 1827791.7224 | 1305565.516 | 783339.3096 | 261113.1032 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09 | -3.8999e-09
3PH | OH | CAPEX | Pre-tax Return on Rate Base |  |  | 3185678.9047 | 3090011.624 | 2981260.3731 | 2877166.962 | 2777382.7231 | 2681585.8097 | 2589476.7253 | 2500778.3239 | 2413984.1834 | 2327462.7187 | 2240941.254 | 2154419.7893 | 2067898.3245 | 1981376.8598 | 1894855.3951 | 1808333.9304 | 1721812.4657 | 1635291.001 | 1548769.5363 | 1462248.0716 | 1385699.3905 | 1329091.8066 | 1282457.0064 | 1235822.2062 | 1189187.4059 | 1142552.6057 | 1095917.8055 | 1049283.0052 | 1002648.205 | 956013.4048 | 909378.6045 | 862743.8043 | 816109.0041 | 769474.2038 | 722839.4036 | 676204.6034 | 629569.8031 | 582935.0029 | 536300.2027 | 489665.4024 | 443030.6022 | 396395.802 | 349761.0017 | 303126.2015 | 256491.4013 | 209856.601 | 163221.8008 | 116587.0006 | 69952.2003 | 23317.4001 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10
3PH | OH | CAPEX | Depreciation Expense |  |  | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 722454.46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3PH | OH | O&M | Outage Restoration - Major/Minor Storm |  |  | 14685.5083 | 16492.253 | 18371.3868 | 20325.2201 | 22356.1304 | 24466.5634 | 26659.035 | 28936.1335 | 31300.5215 | 33754.9374 | 34497.546 | 35256.492 | 36032.1348 | 36824.8418 | 37634.9883 | 38462.958 | 39309.1431 | 40173.9443 | 41057.771 | 41961.042 | 42884.1849 | 43827.637 | 44791.845 | 45777.2656 | 46784.3654 | 47813.6215 | 48865.5212 | 49940.5626 | 51039.255 | 52162.1186 | 53309.6852 | 54482.4983 | 55681.1133 | 56906.0977 | 58158.0319 | 59437.5086 | 60745.1338 | 62081.5267 | 63447.3203 | 64843.1614 | 66269.7109 | 67727.6446 | 69217.6527 | 70740.4411 | 72296.7308 | 73887.2589 | 75512.7786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3PH | OH | O&M | Routine (non-storm) Restoration costs |  |  | 26335.1927 | 26914.5669 | 27506.6874 | 28111.8345 | 28730.2949 | 29362.3614 | 30008.3333 | 30668.5167 | 31343.224 | 32032.775 | 32737.496 | 33457.7209 | 34193.7908 | 34946.0542 | 35714.8674 | 36500.5944 | 37303.6075 | 38124.2869 | 38963.0212 | 39820.2077 | 40696.2522 | 41591.5698 | 42506.5843 | 43441.7292 | 44397.4472 | 45374.1911 | 46372.4233 | 47392.6166 | 48435.2541 | 49500.8297 | 50589.848 | 51702.8246 | 52840.2868 | 54002.7731 | 55190.8341 | 56405.0324 | 57645.9432 | 58914.1539 | 60210.2653 | 61534.8911 | 62888.6587 | 64272.2092 | 65686.1978 | 67131.2942 | 68608.1827 | 70117.5627 | 71660.1491 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3PH | OH | O&M | Pole Inspections | Not included as no change
3PH | OH | O&M | Veg Mng - Tree Trimming | Not included as no change
3PH | OH | O&M | Veg Mng - Tickets | Not included as no change
3PH | OH | O&M | Veg Mng - Danger Trees | Not included as no change
3PH | OH | O&M | Property Taxes |  | 0 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 583381.9765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3PH | OH | O&M | Reduced pole attachment revenue | Not included as no change
|  | Total Costs impacting revenue requirement |  |  |  | 4532536.0421 | 4439254.8805 | 4332974.8837 | 4231440.4531 | 4134305.5849 | 4041251.1709 | 3951980.5301 | 3866219.4106 | 3782464.3653 | 3699086.8674 | 3614012.7324 | 3528970.4386 | 3443960.6866 | 3358984.1922 | 3274041.6872 | 3189133.9194 | 3104261.6528 | 3019425.6686 | 2934626.765 | 2849865.7577 | 2775116.2641 | 2720347.4499 | 2675591.8722 | 2630877.6374 | 2586205.655 | 2541576.8547 | 2496992.1863 | 2452452.6209 | 2407959.1506 | 2363512.7896 | 2319114.5742 | 2274765.5637 | 2230466.8406 | 2186219.5111 | 2142024.706 | 2097883.5809 | 2053797.3165 | 2009767.12 | 1965794.2247 | 1921879.8914 | 1878025.4083 | 1834232.0922 | 1790501.2888 | 1746834.3732 | 1703232.7512 | 1659697.859 | 1616231.1649 | 1422423.437 | 1375788.6368 | 1329153.8366 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10
|  | Subtotal | CAPEX |  |  | 3908133.3647 | 3812466.084 | 3703714.8331 | 3599621.422 | 3499837.1831 | 3404040.2697 | 3311931.1853 | 3223232.7839 | 3136438.6434 | 3049917.1787 | 2963395.714 | 2876874.2493 | 2790352.7845 | 2703831.3198 | 2617309.8551 | 2530788.3904 | 2444266.9257 | 2357745.461 | 2271223.9963 | 2184702.5316 | 2108153.8505 | 2051546.2666 | 2004911.4664 | 1958276.6662 | 1911641.8659 | 1865007.0657 | 1818372.2655 | 1771737.4652 | 1725102.665 | 1678467.8648 | 1631833.0645 | 1585198.2643 | 1538563.4641 | 1491928.6638 | 1445293.8636 | 1398659.0634 | 1352024.2631 | 1305389.4629 | 1258754.6627 | 1212119.8624 | 1165485.0622 | 1118850.262 | 1072215.4617 | 1025580.6615 | 978945.8613 | 932311.061 | 885676.2608 | 839041.4606 | 792406.6603 | 745771.8601 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10 | -3.4826e-10
|  | Subtotal | O&M |  |  | 624402.6774 | 626788.7964 | 629260.0506 | 631819.0311 | 634468.4018 | 637210.9012 | 640049.3448 | 642986.6267 | 646025.7219 | 649169.6888 | 650617.0184 | 652096.1894 | 653607.902 | 655152.8724 | 656731.8321 | 658345.5289 | 659994.7271 | 661680.2076 | 663402.7687 | 665163.2261 | 666962.4136 | 668801.1832 | 670680.4058 | 672600.9712 | 674563.7891 | 676569.789 | 678619.9209 | 680715.1556 | 682856.4856 | 685044.9248 | 687281.5096 | 689567.2994 | 691903.3765 | 694290.8473 | 696730.8424 | 699224.5175 | 701773.0534 | 704377.6571 | 707039.5621 | 709760.0289 | 712540.3461 | 715381.8302 | 718285.827 | 721253.7117 | 724286.8899 | 727386.798 | 730554.9041 | 583381.9765 | 583381.9765 | 583381.9765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Subtotal | O&M - Cost Savings (minus property tax) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Subtotal | O&M - Storm Damage Reductions |  |  | 14685.5083 | 16492.253 | 18371.3868 | 20325.2201 | 22356.1304 | 24466.5634 | 26659.035 | 28936.1335 | 31300.5215 | 33754.9374 | 34497.546 | 35256.492 | 36032.1348 | 36824.8418 | 37634.9883 | 38462.958 | 39309.1431 | 40173.9443 | 41057.771 | 41961.042 | 42884.1849 | 43827.637 | 44791.845 | 45777.2656 | 46784.3654 | 47813.6215 | 48865.5212 | 49940.5626 | 51039.255 | 52162.1186 | 53309.6852 | 54482.4983 | 55681.1133 | 56906.0977 | 58158.0319 | 59437.5086 | 60745.1338 | 62081.5267 | 63447.3203 | 64843.1614 | 66269.7109 | 67727.6446 | 69217.6527 | 70740.4411 | 72296.7308 | 73887.2589 | 75512.7786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
T&D Resilience Projects - Underground (UG) - Detailed Annual Cost Calcs
Phase | Type | Cost Bucket | Cost Category |  | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090
1PH | UG | CAPEX | Plant in Service |  | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 29842862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | CAPEX | Cumulative Depreciation |  | 0 | -596857.24 | -1193714.48 | -1790571.72 | -2387428.96 | -2984286.2 | -3581143.44 | -4178000.68 | -4774857.92 | -5371715.16 | -5968572.4 | -6565429.64 | -7162286.88 | -7759144.12 | -8356001.36 | -8952858.6 | -9549715.84 | -10146573.08 | -10743430.32 | -11340287.56 | -11937144.8 | -12534002.04 | -13130859.28 | -13727716.52 | -14324573.76 | -14921431 | -15518288.24 | -16115145.48 | -16712002.72 | -17308859.96 | -17905717.2 | -18502574.44 | -19099431.68 | -19696288.92 | -20293146.16 | -20890003.4 | -21486860.64 | -22083717.88 | -22680575.12 | -23277432.36 | -23874289.6 | -24471146.84 | -25068004.08 | -25664861.32 | -26261718.56 | -26858575.8 | -27455433.04 | -28052290.28 | -28649147.52 | -29246004.76 | -29842862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | CAPEX | Net Plant (b.o.y.) |  | 0 | 29842862 | 29246004.76 | 28649147.52 | 28052290.28 | 27455433.04 | 26858575.8 | 26261718.56 | 25664861.32 | 25068004.08 | 24471146.84 | 23874289.6 | 23277432.36 | 22680575.12 | 22083717.88 | 21486860.64 | 20890003.4 | 20293146.16 | 19696288.92 | 19099431.68 | 18502574.44 | 17905717.2 | 17308859.96 | 16712002.72 | 16115145.48 | 15518288.24 | 14921431 | 14324573.76 | 13727716.52 | 13130859.28 | 12534002.04 | 11937144.8 | 11340287.56 | 10743430.32 | 10146573.08 | 9549715.84 | 8952858.6 | 8356001.36 | 7759144.12 | 7162286.88 | 6565429.64 | 5968572.4 | 5371715.16 | 4774857.92 | 4178000.68 | 3581143.44 | 2984286.2 | 2387428.96 | 1790571.72 | 1193714.48 | 596857.24 | 2.9802e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | CAPEX | Net Plant (e.o.y.) |  | 29842862 | 29246004.76 | 28649147.52 | 28052290.28 | 27455433.04 | 26858575.8 | 26261718.56 | 25664861.32 | 25068004.08 | 24471146.84 | 23874289.6 | 23277432.36 | 22680575.12 | 22083717.88 | 21486860.64 | 20890003.4 | 20293146.16 | 19696288.92 | 19099431.68 | 18502574.44 | 17905717.2 | 17308859.96 | 16712002.72 | 16115145.48 | 15518288.24 | 14921431 | 14324573.76 | 13727716.52 | 13130859.28 | 12534002.04 | 11937144.8 | 11340287.56 | 10743430.32 | 10146573.08 | 9549715.84 | 8952858.6 | 8356001.36 | 7759144.12 | 7162286.88 | 6565429.64 | 5968572.4 | 5371715.16 | 4774857.92 | 4178000.68 | 3581143.44 | 2984286.2 | 2387428.96 | 1790571.72 | 1193714.48 | 596857.24 | 2.9802e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | CAPEX | MACRS depreciation |  | 0 | 1119107.325 | 2154356.2078 | 1992607.8957 | 1843393.5857 | 1704922.7061 | 1577195.2567 | 1458719.0946 | 1349494.2196 | 1331588.5024 | 1331290.0738 | 1331588.5024 | 1331290.0738 | 1331588.5024 | 1331290.0738 | 1331588.5024 | 1331290.0738 | 1331588.5024 | 1331290.0738 | 1331588.5024 | 1331290.0738 | 665794.2512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | CAPEX | ADIT (b.o.y.) |  | 0 | 0 | -144741.6111 | -576402.45 | -963234.7442 | -1308712.2924 | -1615812.6364 | -1887513.3177 | -2126378.3307 | -2334971.6696 | -2538602.439 | -2742150.4989 | -2945781.2682 | -3149329.3281 | -3352960.0975 | -3556508.1574 | -3760138.9268 | -3963686.9867 | -4167317.7561 | -4370865.816 | -4574496.5854 | -4778044.6453 | -4797150.5379 | -4631731.5538 | -4466312.5698 | -4300893.5857 | -4135474.6016 | -3970055.6176 | -3804636.6335 | -3639217.6495 | -3473798.6654 | -3308379.6813 | -3142960.6973 | -2977541.7132 | -2812122.7291 | -2646703.7451 | -2481284.761 | -2315865.7769 | -2150446.7929 | -1985027.8088 | -1819608.8247 | -1654189.8407 | -1488770.8566 | -1323351.8725 | -1157932.8885 | -992513.9044 | -827094.9203 | -661675.9363 | -496256.9522 | -330837.9681 | -165418.9841 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09
1PH | UG | CAPEX | ADIT (e.o.y.) |  |  | -144741.6111 | -576402.45 | -963234.7442 | -1308712.2924 | -1615812.6364 | -1887513.3177 | -2126378.3307 | -2334971.6696 | -2538602.439 | -2742150.4989 | -2945781.2682 | -3149329.3281 | -3352960.0975 | -3556508.1574 | -3760138.9268 | -3963686.9867 | -4167317.7561 | -4370865.816 | -4574496.5854 | -4778044.6453 | -4797150.5379 | -4631731.5538 | -4466312.5698 | -4300893.5857 | -4135474.6016 | -3970055.6176 | -3804636.6335 | -3639217.6495 | -3473798.6654 | -3308379.6813 | -3142960.6973 | -2977541.7132 | -2812122.7291 | -2646703.7451 | -2481284.761 | -2315865.7769 | -2150446.7929 | -1985027.8088 | -1819608.8247 | -1654189.8407 | -1488770.8566 | -1323351.8725 | -1157932.8885 | -992513.9044 | -827094.9203 | -661675.9363 | -496256.9522 | -330837.9681 | -165418.9841 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09
1PH | UG | CAPEX | Net Rate Base |  |  | 29472062.5745 | 28587004.1095 | 27580900.3029 | 26617888.1417 | 25694741.9556 | 24808484.203 | 23956344.1158 | 23135757.6999 | 22332788.4057 | 21532341.7511 | 20731895.0964 | 19931448.4418 | 19131001.7872 | 18330555.1325 | 17530108.4779 | 16729661.8232 | 15929215.1686 | 15128768.514 | 14328321.8593 | 13527875.2047 | 12819690.9884 | 12295990.2941 | 11864552.0382 | 11433113.7823 | 11001675.5263 | 10570237.2704 | 10138799.0144 | 9707360.7585 | 9275922.5026 | 8844484.2466 | 8413045.9907 | 7981607.7348 | 7550169.4788 | 7118731.2229 | 6687292.967 | 6255854.711 | 5824416.4551 | 5392978.1992 | 4961539.9432 | 4530101.6873 | 4098663.4314 | 3667225.1754 | 3235786.9195 | 2804348.6636 | 2372910.4076 | 1941472.1517 | 1510033.8958 | 1078595.6398 | 647157.3839 | 215719.128 | 1.8452e-08 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09 | 3.5507e-09
1PH | UG | O&M | Pre-tax Return on Rate Base |  |  | 2631855.1879 | 2552819.467 | 2462974.397 | 2376977.4111 | 2294540.4566 | 2215397.6393 | 2139301.5295 | 2066023.1626 | 1994318.0046 | 1922838.1184 | 1851358.2321 | 1779878.3459 | 1708398.4596 | 1636918.5733 | 1565438.6871 | 1493958.8008 | 1422478.9146 | 1350999.0283 | 1279519.142 | 1208039.2558 | 1144798.4053 | 1098031.9333 | 1059504.497 | 1020977.0608 | 982449.6245 | 943922.1882 | 905394.752 | 866867.3157 | 828339.8795 | 789812.4432 | 751285.007 | 712757.5707 | 674230.1345 | 635702.6982 | 597175.262 | 558647.8257 | 520120.3894 | 481592.9532 | 443065.5169 | 404538.0807 | 366010.6444 | 327483.2082 | 288955.7719 | 250428.3357 | 211900.8994 | 173373.4631 | 134846.0269 | 96318.5906 | 57791.1544 | 19263.7181 | 1.6477e-09 | 3.1707e-10 | 3.1707e-10 | 3.1707e-10 | 3.1707e-10 | 3.1707e-10 | 3.1707e-10 | 3.1707e-10 | 3.1707e-10 | 3.1707e-10 | 3.1707e-10 | 3.1707e-10 | 3.1707e-10
1PH | UG | O&M | Depreciation Expense |  |  | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 596857.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | O&M | Outage Restoration - Major/Minor Storm |  |  | 2838.6641 | 3187.9024 | 3551.1332 | 3928.8033 | 4321.3721 | 4729.3123 | 5153.1104 | 5593.2667 | 6050.2957 | 6524.7268 | 6668.2708 | 6814.9727 | 6964.9021 | 7118.13 | 7274.7288 | 7434.7729 | 7598.3379 | 7765.5013 | 7936.3423 | 8110.9419 | 8289.3826 | 8471.749 | 8658.1275 | 8848.6063 | 9043.2756 | 9242.2277 | 9445.5567 | 9653.3589 | 9865.7328 | 10082.779 | 10304.6001 | 10531.3013 | 10762.9899 | 10999.7757 | 11241.7708 | 11489.0897 | 11741.8497 | 12000.1704 | 12264.1742 | 12533.986 | 12809.7337 | 13091.5478 | 13379.5619 | 13673.9122 | 13974.7383 | 14282.1825 | 14596.3906 | 14917.5111 | 15245.6964 | 15581.1017 | 15923.886 | 16274.2114 | 16632.2441 | 16998.1535 | 17372.1128 | 17754.2993 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | O&M | Routine (non-storm) Restoration costs |  |  | 4711.3519 | 4815.0016 | 4920.9317 | 5029.1921 | 5139.8344 | 5252.9107 | 5368.4748 | 5486.5812 | 5607.286 | 5730.6463 | 5856.7205 | 5985.5684 | 6117.2509 | 6251.8304 | 6389.3707 | 6529.9368 | 6673.5954 | 6820.4145 | 6970.4636 | 7123.8138 | 7280.5377 | 7440.7096 | 7604.4052 | 7771.7021 | 7942.6795 | 8117.4185 | 8296.0017 | 8478.5137 | 8665.041 | 8855.6719 | 9050.4967 | 9249.6076 | 9453.099 | 9661.0672 | 9873.6107 | 10090.8301 | 10312.8284 | 10539.7106 | 10771.5842 | 11008.5591 | 11250.7474 | 11498.2638 | 11751.2256 | 12009.7526 | 12273.9671 | 12543.9944 | 12819.9623 | 13102.0015 | 13390.2455 | 13684.8309 | 13985.8972 | 14293.5869 | 14608.0458 | 14929.4228 | 15257.8701 | 15593.5433 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | O&M | Pole Inspections |  |  | 1675.0565 | 1711.9078 | 1749.5698 | 1788.0603 | 1827.3976 | 1867.6004 | 1908.6876 | 1950.6787 | 1993.5936 | 2037.4527 | 2082.2766 | 2128.0867 | 2174.9046 | 2222.7525 | 2271.6531 | 2321.6295 | 2372.7053 | 2424.9048 | 2478.2527 | 2532.7743 | 2588.4953 | 2645.4422 | 2703.642 | 2763.1221 | 2823.9108 | 2886.0368 | 2949.5296 | 3014.4193 | 3080.7365 | 3148.5127 | 3217.78 | 3288.5711 | 3360.9197 | 3434.8599 | 3510.4268 | 3587.6562 | 3666.5847 | 3747.2495 | 3829.689 | 3913.9422 | 4000.0489 | 4088.05 | 4177.9871 | 4269.9028 | 4363.8407 | 4459.8452 | 4557.9618 | 4658.2369 | 4760.7181 | 4865.4539 | 4972.4939 | 5081.8888 | 5193.6903 | 5307.9515 | 5424.7265 | 5544.0704 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | O&M | Veg Mng - Tree Trimming |  |  | 6690.7522 | 6837.9487 | 6988.3836 | 7142.128 | 7299.2548 | 7459.8384 | 7623.9549 | 7791.6819 | 7963.0989 | 8138.2871 | 8317.3294 | 8500.3106 | 8687.3175 | 8878.4385 | 9073.7641 | 9273.3869 | 9477.4014 | 9685.9043 | 9898.9941 | 10116.772 | 10339.341 | 10566.8065 | 10799.2762 | 11036.8603 | 11279.6712 | 11527.824 | 11781.4361 | 12040.6277 | 12305.5216 | 12576.243 | 12852.9204 | 13135.6846 | 13424.6697 | 13720.0124 | 14021.8527 | 14330.3334 | 14645.6008 | 14967.804 | 15297.0957 | 15633.6318 | 15977.5717 | 16329.0783 | 16688.318 | 17055.461 | 17430.6811 | 17814.1561 | 18206.0675 | 18606.601 | 19015.9463 | 19434.2971 | 19861.8516 | 20298.8123 | 20745.3862 | 21201.7847 | 21668.224 | 22144.9249 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | O&M | Veg Mng - Tickets |  |  | 3472.8162 | 3549.2182 | 3627.301 | 3707.1016 | 3788.6578 | 3872.0083 | 3957.1925 | 4044.2507 | 4133.2242 | 4224.1552 | 4317.0866 | 4412.0625 | 4509.1278 | 4608.3287 | 4709.7119 | 4813.3256 | 4919.2187 | 5027.4415 | 5138.0452 | 5251.0822 | 5366.606 | 5484.6714 | 5605.3341 | 5728.6515 | 5854.6818 | 5983.4848 | 6115.1215 | 6249.6542 | 6387.1466 | 6527.6638 | 6671.2724 | 6818.0404 | 6968.0373 | 7121.3341 | 7278.0034 | 7438.1195 | 7601.7581 | 7768.9968 | 7939.9148 | 8114.5929 | 8293.1139 | 8475.5624 | 8662.0248 | 8852.5894 | 9047.3463 | 9246.3879 | 9449.8085 | 9657.7043 | 9870.1738 | 10087.3176 | 10309.2386 | 10536.0418 | 10767.8347 | 11004.7271 | 11246.8311 | 11494.2614 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | O&M | Veg Mng - Danger Trees |  |  | 300.3474 | 306.955 | 313.708 | 320.6096 | 327.663 | 334.8716 | 342.2388 | 349.768 | 357.4629 | 365.3271 | 373.3643 | 381.5783 | 389.973 | 398.5525 | 407.3206 | 416.2817 | 425.4399 | 434.7995 | 444.3651 | 454.1412 | 464.1323 | 474.3432 | 484.7787 | 495.4439 | 506.3436 | 517.4832 | 528.8678 | 540.5029 | 552.394 | 564.5466 | 576.9667 | 589.6599 | 602.6324 | 615.8904 | 629.4399 | 643.2876 | 657.44 | 671.9036 | 686.6855 | 701.7926 | 717.232 | 733.0111 | 749.1374 | 765.6184 | 782.462 | 799.6762 | 817.269 | 835.249 | 853.6244 | 872.4042 | 891.5971 | 911.2122 | 931.2589 | 951.7466 | 972.685 | 994.0841 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | O&M | Property Taxes |  |  | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 481962.2213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | O&M | Reduced pole attachment revenue |  |  | 8933.7681 | 9130.311 | 9331.1778 | 9536.4637 | 9746.2659 | 9960.6838 | 10179.8188 | 10403.7748 | 10632.6579 | 10866.5763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total Costs impacting revenue requirement |  |  |  | 3739297.4055 | 3661178.1729 | 3572276.0633 | 3487249.231 | 3405810.3636 | 3327694.3261 | 3252654.4685 | 3180462.6259 | 3109875.0851 | 3039544.7511 | 2957792.7416 | 2886920.3864 | 2816061.3969 | 2745216.0671 | 2674384.6976 | 2603567.5954 | 2532765.0745 | 2461977.4556 | 2391205.0666 | 2320448.2425 | 2257946.3615 | 2211935.1164 | 2174179.5221 | 2136440.9082 | 2098719.6484 | 2061016.1246 | 2023330.7268 | 1985663.8538 | 1948015.9132 | 1910387.3216 | 1872778.5045 | 1835189.897 | 1797621.9438 | 1760075.0992 | 1722549.8276 | 1685046.6037 | 1647565.9124 | 1610108.2495 | 1572674.1216 | 1535264.0465 | 1497878.5533 | 1460518.1829 | 1423183.488 | 1385875.0333 | 1348593.3963 | 1311339.1668 | 1274112.9479 | 1236915.3557 | 1199747.0202 | 1162608.5848 | 65944.9643 | 67395.7535 | 68878.4601 | 70393.7862 | 71942.4495 | 73525.1834 | 3.1707e-10 | 3.1707e-10 | 3.1707e-10 | 3.1707e-10 | 3.1707e-10 | 3.1707e-10 | 3.1707e-10
|  | Subtotal | CAPEX |  |  | 3228712.4279 | 3149676.707 | 3059831.637 | 2973834.6511 | 2891397.6966 | 2812254.8793 | 2736158.7695 | 2662880.4026 | 2591175.2446 | 2519695.3584 | 2448215.4721 | 2376735.5859 | 2305255.6996 | 2233775.8133 | 2162295.9271 | 2090816.0408 | 2019336.1546 | 1947856.2683 | 1876376.382 | 1804896.4958 | 1741655.6453 | 1694889.1733 | 1656361.737 | 1617834.3008 | 1579306.8645 | 1540779.4282 | 1502251.992 | 1463724.5557 | 1425197.1195 | 1386669.6832 | 1348142.247 | 1309614.8107 | 1271087.3745 | 1232559.9382 | 1194032.502 | 1155505.0657 | 1116977.6294 | 1078450.1932 | 1039922.7569 | 1001395.3207 | 962867.8844 | 924340.4482 | 885813.0119 | 847285.5757 | 808758.1394 | 770230.7031 | 731703.2669 | 693175.8306 | 654648.3944 | 616120.9581 | 1.6477e-09 | 3.1707e-10 | 3.1707e-10 | 3.1707e-10 | 3.1707e-10 | 3.1707e-10 | 3.1707e-10 | 3.1707e-10 | 3.1707e-10 | 3.1707e-10 | 3.1707e-10 | 3.1707e-10 | 3.1707e-10
|  | Subtotal | O&M |  |  | 510584.9776 | 511501.4659 | 512444.4263 | 513414.5799 | 514412.6669 | 515439.4468 | 516495.699 | 517582.2233 | 518699.8405 | 519849.3927 | 509577.2695 | 510184.8006 | 510805.6973 | 511440.2538 | 512088.7705 | 512751.5546 | 513428.9199 | 514121.1873 | 514828.6845 | 515551.7467 | 516290.7163 | 517045.9432 | 517817.785 | 518606.6074 | 519412.7839 | 520236.6963 | 521078.7348 | 521939.2981 | 522818.7938 | 523717.6383 | 524636.2575 | 525575.0863 | 526534.5693 | 527515.161 | 528517.3257 | 529541.538 | 530588.2829 | 531658.0563 | 532751.3647 | 533868.7258 | 535010.6689 | 536177.7348 | 537370.4761 | 538589.4577 | 539835.2569 | 541108.4637 | 542409.681 | 543739.5251 | 545098.6258 | 546487.6267 | 65944.9643 | 67395.7535 | 68878.4601 | 70393.7862 | 71942.4495 | 73525.1834 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Subtotal | O&M - Cost Savings (minus property tax) |  |  | 21072.7403 | 21536.3406 | 22010.1401 | 22494.3632 | 22989.2392 | 23495.0025 | 24011.8925 | 24540.1541 | 25080.0375 | 25631.7984 | 15090.0569 | 15422.0382 | 15761.323 | 16108.0721 | 16462.4497 | 16824.6236 | 17194.7653 | 17573.0501 | 17959.6573 | 18354.7697 | 18758.5746 | 19171.2633 | 19593.0311 | 20024.0778 | 20464.6075 | 20914.8288 | 21374.9551 | 21845.2041 | 22325.7986 | 22816.9661 | 23318.9394 | 23831.9561 | 24356.2591 | 24892.0968 | 25439.7229 | 25999.3968 | 26571.3836 | 27155.954 | 27753.385 | 28363.9595 | 28987.9666 | 29625.7018 | 30277.4673 | 30943.5716 | 31624.3301 | 32320.0654 | 33031.1068 | 33757.7912 | 34500.4626 | 35259.4728 | 36035.1812 | 36827.9551 | 37638.1702 | 38466.2099 | 39312.4665 | 40177.3408 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Subtotal | O&M - Storm Damage Reductions |  |  | 2838.6641 | 3187.9024 | 3551.1332 | 3928.8033 | 4321.3721 | 4729.3123 | 5153.1104 | 5593.2667 | 6050.2957 | 6524.7268 | 6668.2708 | 6814.9727 | 6964.9021 | 7118.13 | 7274.7288 | 7434.7729 | 7598.3379 | 7765.5013 | 7936.3423 | 8110.9419 | 8289.3826 | 8471.749 | 8658.1275 | 8848.6063 | 9043.2756 | 9242.2277 | 9445.5567 | 9653.3589 | 9865.7328 | 10082.779 | 10304.6001 | 10531.3013 | 10762.9899 | 10999.7757 | 11241.7708 | 11489.0897 | 11741.8497 | 12000.1704 | 12264.1742 | 12533.986 | 12809.7337 | 13091.5478 | 13379.5619 | 13673.9122 | 13974.7383 | 14282.1825 | 14596.3906 | 14917.5111 | 15245.6964 | 15581.1017 | 15923.886 | 16274.2114 | 16632.2441 | 16998.1535 | 17372.1128 | 17754.2993 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rollup costs
[6 empty] | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090
|  |  | Pre-tax Return on Rate Base |  |  | 6702198.0789 | 6500928.2448 | 6272131.669 | 6053134.5004 | 5843203.1941 | 5641660.6318 | 5447876.7173 | 5261268.3764 | 5078666.319 | 4896637.9314 | 4714609.5437 | 4532581.1561 | 4350552.7684 | 4168524.3808 | 3986495.9932 | 3804467.6055 | 3622439.2179 | 3440410.8302 | 3258382.4426 | 3076354.0549 | 2915306.9317 | 2796212.9328 | 2698100.1983 | 2599987.4638 | 2501874.7294 | 2403761.9949 | 2305649.2604 | 2207536.5259 | 2109423.7914 | 2011311.0569 | 1913198.3224 | 1815085.588 | 1716972.8535 | 1618860.119 | 1520747.3845 | 1422634.65 | 1324521.9155 | 1226409.1811 | 1128296.4466 | 1030183.7121 | 932070.9776 | 833958.2431 | 735845.5086 | 637732.7741 | 539620.0397 | 441507.3052 | 343394.5707 | 245281.8362 | 147169.1017 | 49056.3672 | 1.384e-09 | 5.3279e-11 | 5.3279e-11 | 5.3279e-11 | 5.3279e-11 | 5.3279e-11 | 5.3279e-11 | 5.3279e-11 | 5.3279e-11 | 5.3279e-11
|  |  | Depreciation Expense |  |  | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 1519937.52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Outage Restoration - Major/Minor Storm |  |  | 23232.9777 | 26091.3099 | 29064.1639 | 32155.1953 | 35368.165 | 38706.9423 | 42175.5076 | 45777.9556 | 49518.4984 | 53401.4685 | 54576.3008 | 55776.9794 | 57004.073 | 58258.1626 | 59539.8422 | 60849.7187 | 62188.4125 | 63556.5576 | 64954.8018 | 66383.8075 | 67844.2512 | 69336.8248 | 70862.2349 | 72421.2041 | 74014.4706 | 75642.7889 | 77306.9303 | 79007.6828 | 80745.8518 | 82522.2605 | 84337.7502 | 86193.1807 | 88089.4307 | 90027.3982 | 92008.001 | 94032.177 | 96100.8849 | 98215.1043 | 100375.8366 | 102584.105 | 104840.9554 | 107147.4564 | 109504.7004 | 111913.8038 | 114375.9075 | 116892.1775 | 119463.8054 | 14917.5111 | 15245.6964 | 15581.1017 | 15923.886 | 16274.2114 | 16632.2441 | 16998.1535 | 17372.1128 | 17754.2993 | 0 | 0 | 0 | 0
|  |  | Routine (non-storm) Restoration costs |  |  | 33383.0284 | 34117.4551 | 34868.0391 | 35635.1359 | 36419.1089 | 37220.3293 | 38039.1766 | 38876.0384 | 39731.3113 | 40605.4001 | 41498.7189 | 42411.6908 | 43344.748 | 44298.3324 | 45272.8957 | 46268.8994 | 47286.8152 | 48327.1252 | 49390.3219 | 50476.909 | 51587.401 | 52722.3238 | 53882.2149 | 55067.6237 | 56279.1114 | 57517.2518 | 58782.6314 | 60075.8493 | 61397.5179 | 62748.2633 | 64128.7251 | 65539.5571 | 66981.4273 | 68455.0187 | 69961.0292 | 71500.1718 | 73073.1756 | 74680.7854 | 76323.7627 | 78002.8855 | 79718.949 | 81472.7659 | 83265.1667 | 85097.0004 | 86969.1344 | 88882.4553 | 90837.8694 | 13102.0015 | 13390.2455 | 13684.8309 | 13985.8972 | 14293.5869 | 14608.0458 | 14929.4228 | 15257.8701 | 15593.5433 | 0 | 0 | 0 | 0
|  |  | Pole Inspections |  |  | 1675.0565 | 1711.9078 | 1749.5698 | 1788.0603 | 1827.3976 | 1867.6004 | 1908.6876 | 1950.6787 | 1993.5936 | 2037.4527 | 2082.2766 | 2128.0867 | 2174.9046 | 2222.7525 | 2271.6531 | 2321.6295 | 2372.7053 | 2424.9048 | 2478.2527 | 2532.7743 | 2588.4953 | 2645.4422 | 2703.642 | 2763.1221 | 2823.9108 | 2886.0368 | 2949.5296 | 3014.4193 | 3080.7365 | 3148.5127 | 3217.78 | 3288.5711 | 3360.9197 | 3434.8599 | 3510.4268 | 3587.6562 | 3666.5847 | 3747.2495 | 3829.689 | 3913.9422 | 4000.0489 | 4088.05 | 4177.9871 | 4269.9028 | 4363.8407 | 4459.8452 | 4557.9618 | 4658.2369 | 4760.7181 | 4865.4539 | 4972.4939 | 5081.8888 | 5193.6903 | 5307.9515 | 5424.7265 | 5544.0704 | 0 | 0 | 0 | 0
|  |  | Veg Mng - Tree Trimming |  |  | 6690.7522 | 6837.9487 | 6988.3836 | 7142.128 | 7299.2548 | 7459.8384 | 7623.9549 | 7791.6819 | 7963.0989 | 8138.2871 | 8317.3294 | 8500.3106 | 8687.3175 | 8878.4385 | 9073.7641 | 9273.3869 | 9477.4014 | 9685.9043 | 9898.9941 | 10116.772 | 10339.341 | 10566.8065 | 10799.2762 | 11036.8603 | 11279.6712 | 11527.824 | 11781.4361 | 12040.6277 | 12305.5216 | 12576.243 | 12852.9204 | 13135.6846 | 13424.6697 | 13720.0124 | 14021.8527 | 14330.3334 | 14645.6008 | 14967.804 | 15297.0957 | 15633.6318 | 15977.5717 | 16329.0783 | 16688.318 | 17055.461 | 17430.6811 | 17814.1561 | 18206.0675 | 18606.601 | 19015.9463 | 19434.2971 | 19861.8516 | 20298.8123 | 20745.3862 | 21201.7847 | 21668.224 | 22144.9249 | 0 | 0 | 0 | 0
|  |  | Veg Mng - Tickets |  |  | 3472.8162 | 3549.2182 | 3627.301 | 3707.1016 | 3788.6578 | 3872.0083 | 3957.1925 | 4044.2507 | 4133.2242 | 4224.1552 | 4317.0866 | 4412.0625 | 4509.1278 | 4608.3287 | 4709.7119 | 4813.3256 | 4919.2187 | 5027.4415 | 5138.0452 | 5251.0822 | 5366.606 | 5484.6714 | 5605.3341 | 5728.6515 | 5854.6818 | 5983.4848 | 6115.1215 | 6249.6542 | 6387.1466 | 6527.6638 | 6671.2724 | 6818.0404 | 6968.0373 | 7121.3341 | 7278.0034 | 7438.1195 | 7601.7581 | 7768.9968 | 7939.9148 | 8114.5929 | 8293.1139 | 8475.5624 | 8662.0248 | 8852.5894 | 9047.3463 | 9246.3879 | 9449.8085 | 9657.7043 | 9870.1738 | 10087.3176 | 10309.2386 | 10536.0418 | 10767.8347 | 11004.7271 | 11246.8311 | 11494.2614 | 0 | 0 | 0 | 0
|  |  | Veg Mng - Danger Trees |  |  | 300.3474 | 306.955 | 313.708 | 320.6096 | 327.663 | 334.8716 | 342.2388 | 349.768 | 357.4629 | 365.3271 | 373.3643 | 381.5783 | 389.973 | 398.5525 | 407.3206 | 416.2817 | 425.4399 | 434.7995 | 444.3651 | 454.1412 | 464.1323 | 474.3432 | 484.7787 | 495.4439 | 506.3436 | 517.4832 | 528.8678 | 540.5029 | 552.394 | 564.5466 | 576.9667 | 589.6599 | 602.6324 | 615.8904 | 629.4399 | 643.2876 | 657.44 | 671.9036 | 686.6855 | 701.7926 | 717.232 | 733.0111 | 749.1374 | 765.6184 | 782.462 | 799.6762 | 817.269 | 835.249 | 853.6244 | 872.4042 | 891.5971 | 911.2122 | 931.2589 | 951.7466 | 972.685 | 994.0841 | 0 | 0 | 0 | 0
|  |  | Property Taxes |  |  | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 1227349.5474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Reduced pole attachment revenue |  |  | 8933.7681 | 9130.311 | 9331.1778 | 9536.4637 | 9746.2659 | 9960.6838 | 10179.8188 | 10403.7748 | 10632.6579 | 10866.5763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Benefits_Baseline
|  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63
T&D Resilience Projects - Overhead Spacer (OH) Cable - Detailed Annual Benefit Calcs
Phase | Type | Benefit Category | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090
1PH | OH | Customer Costs of Outages - Res |  | 32161.4286 | 30420.313 | 28697.2895 | 26991.4573 | 25301.9257 | 23627.8134 | 21968.2484 | 20322.3676 | 18689.3159 | 17068.2461 | 17443.7475 | 17827.5099 | 18219.7152 | 18620.5489 | 19030.201 | 19448.8654 | 19876.7404 | 20314.0287 | 20760.9374 | 21217.678 | 21684.4669 | 22161.5252 | 22649.0787 | 23147.3584 | 23656.6003 | 24177.0455 | 24708.9405 | 25252.5372 | 25808.0931 | 26375.8711 | 26956.1403 | 27549.1754 | 28155.2572 | 28774.6729 | 29407.7157 | 30054.6854 | 30715.8885 | 31391.638 | 32082.2541 | 32788.0637 | 33509.4011 | 34246.6079 | 35000.0333 | 35770.034 | 36556.9747 | 37361.2282 | 38183.1752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | OH | Customer Costs of Outages - Nonres |  | 982625.3546 | 929429.1982 | 876785.8105 | 824667.667 | 773047.5518 | 721898.5431 | 671193.9991 | 620907.5446 | 571013.0563 | 521484.6501 | 532957.3124 | 544682.3732 | 556665.3854 | 568912.0239 | 581428.0884 | 594219.5064 | 607292.3355 | 620652.7669 | 634307.1278 | 648261.8846 | 662523.6461 | 677099.1663 | 691995.3479 | 707219.2456 | 722778.069 | 738679.1865 | 754930.1286 | 771538.5914 | 788512.4404 | 805859.7141 | 823588.6278 | 841707.5777 | 860225.1444 | 879150.0975 | 898491.3997 | 918258.2105 | 938459.8911 | 959106.0087 | 980206.3409 | 1001770.8804 | 1023809.8398 | 1046333.6563 | 1069352.9967 | 1092878.7626 | 1116922.0954 | 1141494.3815 | 1166607.2579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | OH | Feeder Backup - Customer Costs of Outages - Res |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | OH | Feeder Backup - Customer Costs of Outages - Nonres |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | OH | Value of avoided line losses |  | 34.2027 | 68.0006 | 98.0426 | 129.6143 | 162.8452 | 195.2905 | 227.4678 | 259.5834 | 291.6538 | 323.6951 | 330.8164 | 338.0943 | 345.5324 | 353.1341 | 360.9031 | 368.8429 | 376.9575 | 385.2505 | 393.7261 | 402.388 | 411.2406 | 420.2879 | 429.5342 | 438.9839 | 448.6416 | 458.5117 | 468.599 | 478.9081 | 489.4441 | 500.2119 | 511.2166 | 522.4633 | 533.9575 | 545.7046 | 557.7101 | 569.9797 | 582.5193 | 595.3347 | 608.432 | 621.8175 | 635.4975 | 649.4785 | 663.767 | 678.3699 | 693.294 | 708.5465 | 724.1345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total Benefits |  | 1014820.986 | 959917.5118 | 905581.1426 | 851788.7387 | 798512.3227 | 745721.6469 | 693389.7154 | 641489.4956 | 589994.026 | 538876.5912 | 550731.8762 | 562847.9775 | 575230.633 | 587885.7069 | 600819.1925 | 614037.2147 | 627546.0334 | 641352.0462 | 655461.7912 | 669881.9506 | 684619.3535 | 699680.9793 | 715073.9608 | 730805.588 | 746883.3109 | 763314.7438 | 780107.6681 | 797270.0368 | 814809.9776 | 832735.7971 | 851055.9847 | 869779.2163 | 888914.3591 | 908470.475 | 928456.8254 | 948882.8756 | 969758.2989 | 991092.9814 | 1012897.027 | 1035180.7616 | 1057954.7384 | 1081229.7426 | 1105016.797 | 1129327.1665 | 1154172.3642 | 1179564.1562 | 1205514.5676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Benefit Category | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090
3PH | OH | Customer Costs of Outages - Res |  | 463084.2442 | 438014.362 | 413204.9845 | 388643.1401 | 364316.0026 | 340210.8847 | 316315.2308 | 292616.6109 | 269102.7138 | 245761.3412 | 251168.0907 | 256693.7887 | 262341.0521 | 268112.5552 | 274011.0314 | 280039.2741 | 286200.1381 | 292496.5412 | 298931.4651 | 305507.9573 | 312229.1324 | 319098.1733 | 326118.3331 | 333292.9364 | 340625.381 | 348119.1394 | 355777.7605 | 363604.8712 | 371604.1784 | 379779.4703 | 388134.6186 | 396673.5802 | 405400.399 | 414319.2078 | 423434.2304 | 432749.7834 | 442270.2787 | 452000.2248 | 461944.2297 | 472107.0028 | 482493.3569 | 493108.2107 | 503956.5913 | 515043.6364 | 526374.5964 | 537954.8375 | 549789.8439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3PH | OH | Customer Costs of Outages - Nonres |  | 13581588.5932 | 12846325.3436 | 12118702.3175 | 11398339.0789 | 10684859.4555 | 9977891.3416 | 9277066.5032 | 8582020.3855 | 7892391.9227 | 7207823.3493 | 7366395.463 | 7528456.1632 | 7694082.1988 | 7863352.0071 | 8036345.7513 | 8213145.3578 | 8393834.5557 | 8578498.9159 | 8767225.8921 | 8960104.8617 | 9157227.1687 | 9358686.1664 | 9564577.262 | 9774997.9618 | 9990047.917 | 10209828.9711 | 10434445.2085 | 10664003.0031 | 10898611.0691 | 11138380.5127 | 11383424.8839 | 11633860.2314 | 11889805.1565 | 12151380.8699 | 12418711.2491 | 12691922.8965 | 12971145.2003 | 13256510.3947 | 13548153.6234 | 13846213.0031 | 14150829.6891 | 14462147.9423 | 14780315.197 | 15105482.1314 | 15437802.7383 | 15777434.3985 | 16124537.9553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3PH | OH | Feeder Backup - Customer Costs of Outages - Res |  | 11132.8239 | 22254.1632 | 33369.6706 | 44484.9874 | 55605.7459 | 66737.5725 | 77886.0907 | 89056.9237 | 100255.6973 | 111488.043 | 113940.78 | 116447.4771 | 119009.3216 | 121627.5267 | 124303.3323 | 127038.0056 | 129832.8417 | 132689.1642 | 135608.3259 | 138591.709 | 141640.7266 | 144756.8226 | 147941.4727 | 151196.1851 | 154522.5012 | 157921.9962 | 161396.2801 | 164946.9983 | 168575.8322 | 172284.5006 | 176074.7596 | 179948.4043 | 183907.2692 | 187953.2291 | 192088.2001 | 196314.1405 | 200633.0516 | 205046.9788 | 209558.0123 | 214168.2886 | 218879.9909 | 223695.3507 | 228616.6484 | 233646.2147 | 238786.4314 | 244039.7329 | 249408.607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3PH | OH | Feeder Backup - Customer Costs of Outages - Nonres |  | 68352.5201 | 78155.9982 | 87983.9969 | 97841.4584 | 336631.3917 | 672915.5144 | 1009023.2959 | 1345125.3116 | 1681391.8716 | 2017993.1075 | 2062388.9559 | 2107761.5129 | 2154132.2662 | 2201523.176 | 2249956.6859 | 2299455.733 | 2350043.7591 | 2401744.7218 | 2454583.1057 | 2508583.934 | 2563772.7806 | 2620175.7817 | 2677819.6489 | 2736731.6812 | 2796939.7782 | 2858472.4533 | 2921358.8473 | 2985628.7419 | 3051312.5743 | 3118441.4509 | 3187047.1628 | 3257162.2004 | 3328819.7688 | 3402053.8037 | 3476898.9874 | 3553390.7651 | 3631565.3619 | 3711459.7999 | 3793111.9155 | 3876560.3776 | 3961844.706 | 4049005.2895 | 4138083.4059 | 4229121.2408 | 4322161.9081 | 4417249.4701 | 4514428.9584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3PH | OH | Value of avoided line losses |  | 1789.2893 | 3557.3968 | 5129.0216 | 6780.6715 | 8519.1192 | 10216.4683 | 11899.7974 | 13579.9017 | 15257.6369 | 16933.8528 | 17306.3976 | 17687.1383 | 18076.2554 | 18473.933 | 18880.3595 | 19295.7274 | 19720.2334 | 20154.0786 | 20597.4683 | 21050.6126 | 21513.7261 | 21987.0281 | 22470.7427 | 22965.099 | 23470.3312 | 23986.6785 | 24514.3854 | 25053.7019 | 25604.8833 | 26168.1908 | 26743.891 | 27332.2566 | 27933.5662 | 28548.1047 | 29176.163 | 29818.0385 | 30474.0354 | 31144.4642 | 31829.6424 | 32529.8945 | 33245.5522 | 33976.9543 | 34724.4473 | 35488.3852 | 36269.1297 | 37067.0505 | 37882.5256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total Benefits |  | 14125947.4707 | 13388307.2638 | 12658389.9911 | 11936089.3362 | 11449931.7149 | 11067971.7815 | 10692190.918 | 10322399.1333 | 9958399.8423 | 9599999.6939 | 9811199.6871 | 10027046.0802 | 10247641.094 | 10473089.1981 | 10703497.1604 | 10938974.098 | 11179631.5281 | 11425583.4217 | 11676946.257 | 11933839.0747 | 12196383.5343 | 12464703.9721 | 12738927.4594 | 13019183.8636 | 13305605.9085 | 13598329.2385 | 13897492.4818 | 14203237.3164 | 14515708.5373 | 14835054.1252 | 15161425.3159 | 15494976.6729 | 15835866.1597 | 16184255.2152 | 16540308.8299 | 16904195.6242 | 17276087.9279 | 17656161.8623 | 18044597.4233 | 18441578.5666 | 18847293.2951 | 19261933.7476 | 19685696.29 | 20118781.6084 | 20561394.8038 | 21013745.4895 | 21476047.8902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
T&D Resilience Projects - Underground (UG) - Detailed Annual Benefit Calcs
Phase | Type | Benefit Category | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090
1PH | UG | Customer Costs of Outages - Res |  | 86232.0189 | 80634.6637 | 75086.776 | 69585.4687 | 64127.8827 | 58711.1854 | 53332.5692 | 47989.2503 | 42678.4669 | 37397.4781 | 38220.2226 | 39061.0675 | 39920.411 | 40798.66 | 41696.2305 | 42613.5476 | 43551.0457 | 44509.1687 | 45488.3704 | 46489.1145 | 47511.875 | 48557.1363 | 49625.3933 | 50717.1519 | 51832.9293 | 52973.2537 | 54138.6653 | 55329.7159 | 56546.9697 | 57791.003 | 59062.4051 | 60361.778 | 61689.7371 | 63046.9113 | 64433.9434 | 65851.4901 | 67300.2229 | 68780.8278 | 70294.006 | 71840.4742 | 73420.9646 | 75036.2258 | 76687.0228 | 78374.1373 | 80098.3683 | 81860.5324 | 83661.4641 | 85502.0163 | 87383.0607 | 89305.488 | 91270.2088 | 93278.1534 | 95330.2727 | 97427.5387 | 99570.9446 | 101761.5054 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | Customer Costs of Outages - Nonres |  | 2349212.4214 | 2196724.0925 | 2045583.4053 | 1895711.7043 | 1747031.0984 | 1599464.4194 | 1452935.1825 | 1307367.5462 | 1162686.2727 | 1018816.6894 | 1041230.6566 | 1064137.731 | 1087548.7611 | 1111474.8338 | 1135927.2802 | 1160917.6803 | 1186457.8693 | 1212559.9424 | 1239236.2612 | 1266499.4589 | 1294362.447 | 1322838.4208 | 1351940.8661 | 1381683.5651 | 1412080.6036 | 1443146.3769 | 1474895.5971 | 1507343.3003 | 1540504.8529 | 1574395.9596 | 1609032.6708 | 1644431.3895 | 1680608.8801 | 1717582.2755 | 1755369.0855 | 1793987.2054 | 1833454.9239 | 1873790.9322 | 1915014.3327 | 1957144.6481 | 2000201.8303 | 2044206.2706 | 2089178.8085 | 2135140.7423 | 2182113.8387 | 2230120.3431 | 2279182.9907 | 2329325.0165 | 2380570.1668 | 2432942.7105 | 2486467.4501 | 2541169.734 | 2597075.4682 | 2654211.1285 | 2712603.7733 | 2772281.0563 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | Feeder Backup - Customer Costs of Outages - Res |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | Feeder Backup - Customer Costs of Outages - Nonres |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | Value of avoided line losses |  | 413.5614 | 822.227 | 1185.4792 | 1567.2278 | 1969.0381 | 2361.3492 | 2750.4198 | 3138.7451 | 3526.5228 | 3913.9494 | 4000.0563 | 4088.0575 | 4177.9948 | 4269.9106 | 4363.8487 | 4459.8534 | 4557.9701 | 4658.2455 | 4760.7269 | 4865.4629 | 4972.503 | 5081.8981 | 5193.6999 | 5307.9613 | 5424.7364 | 5544.0806 | 5666.0504 | 5790.7035 | 5918.099 | 6048.2972 | 6181.3597 | 6317.3496 | 6456.3313 | 6598.3706 | 6743.5347 | 6891.8925 | 7043.5141 | 7198.4714 | 7356.8378 | 7518.6883 | 7684.0994 | 7853.1496 | 8025.9189 | 8202.4891 | 8382.9438 | 8567.3686 | 8755.8507 | 8948.4794 | 9145.346 | 9346.5436 | 9552.1676 | 9762.3152 | 9977.0862 | 10196.5821 | 10420.9069 | 10650.1668 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total Benefits |  | 2435858.0017 | 2278180.9832 | 2121855.6605 | 1966864.4009 | 1813128.0192 | 1660536.954 | 1509018.1716 | 1358495.5416 | 1208891.2625 | 1060128.1168 | 1083450.9354 | 1107286.856 | 1131647.1668 | 1156543.4045 | 1181987.3594 | 1207991.0813 | 1234566.8851 | 1261727.3565 | 1289485.3584 | 1317854.0363 | 1346846.8251 | 1376477.4552 | 1406759.9592 | 1437708.6783 | 1469338.2693 | 1501663.7112 | 1534700.3128 | 1568463.7197 | 1602969.9216 | 1638235.2598 | 1674276.4355 | 1711110.5171 | 1748754.9485 | 1787227.5574 | 1826546.5636 | 1866730.588 | 1907798.661 | 1949770.2315 | 1992665.1766 | 2036503.8105 | 2081306.8943 | 2127095.646 | 2173891.7502 | 2221717.3687 | 2270595.1508 | 2320548.2441 | 2371600.3055 | 2423775.5122 | 2477098.5735 | 2531594.7421 | 2587289.8264 | 2644210.2026 | 2702382.8271 | 2761835.2493 | 2822595.6248 | 2884692.7285 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Benefits_Mitigation
|  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63
T&D Resilience Program - Overhead Spacer Cable (OH) - Project Type Detailed Annual Benefit Calcs
Phase | Type | Benefit Category | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090
1PH | OH | Customer Costs of Outages - Res |  | 9603.8886 | 9815.1742 | 10031.108 | 10251.7924 | 10477.3318 | 10707.8331 | 10943.4054 | 11184.1604 | 11430.2119 | 11681.6766 | 11938.6734 | 12201.3242 | 12469.7534 | 12744.088 | 13024.4579 | 13310.996 | 13603.8379 | 13903.1223 | 14208.991 | 14521.5888 | 14841.0638 | 15167.5672 | 15501.2536 | 15842.2812 | 16190.8114 | 16547.0093 | 16911.0435 | 17283.0864 | 17663.3143 | 18051.9072 | 18449.0492 | 18854.9283 | 19269.7367 | 19693.6709 | 20126.9317 | 20569.7242 | 21022.2581 | 21484.7478 | 21957.4122 | 22440.4753 | 22934.1657 | 23438.7174 | 23954.3692 | 24481.3653 | 25019.9553 | 25570.3943 | 26132.943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | OH | Customer Costs of Outages - Nonres |  | 214424.3577 | 219141.6936 | 223962.8109 | 228889.9927 | 233925.5726 | 239071.9352 | 244331.5177 | 249706.8111 | 255200.361 | 260814.7689 | 266552.6938 | 272416.8531 | 278410.0238 | 284535.0444 | 290794.8153 | 297192.3013 | 303730.5319 | 310412.6036 | 317241.6809 | 324220.9979 | 331353.8598 | 338643.6447 | 346093.8049 | 353707.8686 | 361489.4417 | 369442.2095 | 377569.9381 | 385876.4767 | 394365.7592 | 403041.8059 | 411908.7256 | 420970.7176 | 430232.0734 | 439697.179 | 449370.5169 | 459256.6683 | 469360.315 | 479686.2419 | 490239.3393 | 501024.6047 | 512047.146 | 523312.1832 | 534825.0513 | 546591.2024 | 558616.2089 | 570905.7655 | 583465.6923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | OH | Feeder Backup - Customer Costs of Outages - Res |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | OH | Feeder Backup - Customer Costs of Outages - Nonres |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | OH | Value of avoided line losses |  | 342.0274 | 347.6623 | 341.6411 | 346.2562 | 355.6839 | 363.2206 | 370.4851 | 377.8948 | 385.4527 | 393.1617 | 401.8113 | 410.6511 | 419.6854 | 428.9185 | 438.3547 | 447.9985 | 457.8545 | 467.9273 | 478.2217 | 488.7426 | 499.4949 | 510.4838 | 521.7144 | 533.1922 | 544.9224 | 556.9107 | 569.1627 | 581.6843 | 594.4813 | 607.5599 | 620.9262 | 634.5866 | 648.5475 | 662.8156 | 677.3975 | 692.3003 | 707.5309 | 723.0966 | 739.0047 | 755.2628 | 771.8786 | 788.8599 | 806.2148 | 823.9515 | 842.0785 | 860.6042 | 879.5375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 224370.2738 | 229304.5301 | 234335.5599 | 239488.0413 | 244758.5883 | 250142.9889 | 255645.4082 | 261268.8662 | 267016.0255 | 272889.6072 | 278893.1785 | 285028.8284 | 291299.4627 | 297708.0508 | 304257.628 | 310951.2958 | 317792.2243 | 324783.6532 | 331928.8936 | 339231.3292 | 346694.4185 | 354321.6957 | 362116.773 | 370083.342 | 378225.1755 | 386546.1294 | 395050.1442 | 403741.2474 | 412623.5549 | 421701.2731 | 430978.7011 | 440460.2325 | 450150.3576 | 460053.6655 | 470174.8461 | 480518.6927 | 491090.104 | 501894.0863 | 512935.7562 | 524220.3428 | 535753.1903 | 547539.7605 | 559585.6353 | 571896.5192 | 584478.2427 | 597336.764 | 610478.1728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Benefit Category | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090
3PH | OH | Customer Costs of Outages - Res |  | 138283.9535 | 141326.2005 | 144435.3769 | 147612.9552 | 150860.4402 | 154179.3699 | 157571.3161 | 161037.885 | 164580.7185 | 168201.4943 | 171901.9272 | 175683.7696 | 179548.8125 | 183498.8864 | 187535.8619 | 191661.6508 | 195878.2071 | 200187.5277 | 204591.6533 | 209092.6697 | 213692.7084 | 218393.948 | 223198.6149 | 228108.9844 | 233127.382 | 238256.1844 | 243497.8205 | 248854.7726 | 254329.5776 | 259924.8283 | 265643.1745 | 271487.3243 | 277460.0455 | 283564.1665 | 289802.5781 | 296178.2348 | 302694.156 | 309353.4274 | 316159.2028 | 323114.7053 | 330223.2288 | 337488.1398 | 344912.8789 | 352500.9623 | 360255.9834 | 368181.6151 | 376281.6106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3PH | OH | Customer Costs of Outages - Nonres |  | 2963716.9421 | 3028918.7148 | 3095554.9266 | 3163657.1349 | 3233257.5919 | 3304389.2589 | 3377085.8226 | 3451381.7107 | 3527312.1084 | 3604912.9748 | 3684221.0602 | 3765273.9235 | 3848109.9498 | 3932768.3687 | 4019289.2729 | 4107713.6369 | 4198083.3369 | 4290441.1703 | 4384830.876 | 4481297.1553 | 4579885.6927 | 4680643.1779 | 4783617.3279 | 4888856.9091 | 4996411.7611 | 5106332.8198 | 5218672.1419 | 5333482.929 | 5450819.5534 | 5570737.5836 | 5693293.8104 | 5818546.2743 | 5946554.2923 | 6077378.4867 | 6211080.8134 | 6347724.5913 | 6487374.5323 | 6630096.772 | 6775958.901 | 6925029.9969 | 7077380.6568 | 7233083.0312 | 7392210.8579 | 7554839.4968 | 7721045.9657 | 7890908.977 | 8064508.9745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3PH | OH | Feeder Backup - Customer Costs of Outages - Res |  | 111328.2391 | 113777.4603 | 116280.5644 | 118838.7369 | 121453.1891 | 124125.1592 | 126855.9127 | 129646.7428 | 132498.9712 | 135413.9485 | 138393.0554 | 141437.7026 | 144549.3321 | 147729.4174 | 150979.4646 | 154301.0128 | 157695.6351 | 161164.939 | 164710.5677 | 168334.2002 | 172037.5526 | 175822.3787 | 179690.4711 | 183643.6614 | 187683.822 | 191812.8661 | 196032.7491 | 200345.4696 | 204753.0699 | 209257.6375 | 213861.3055 | 218566.2542 | 223374.7118 | 228288.9555 | 233311.3125 | 238444.1614 | 243689.9329 | 249051.1114 | 254530.2359 | 260129.9011 | 265852.7589 | 271701.5196 | 277678.953 | 283787.89 | 290031.2236 | 296411.9105 | 302932.9725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3PH | OH | Feeder Backup - Customer Costs of Outages - Nonres |  | 3085681.0215 | 3153566.004 | 3222944.4561 | 3293849.2341 | 3366313.9172 | 3440372.8234 | 3516061.0255 | 3593414.3681 | 3672469.4842 | 3753263.8128 | 3835835.6167 | 3920224.0003 | 4006468.9283 | 4094611.2447 | 4184692.6921 | 4276755.9313 | 4370844.5618 | 4467003.1422 | 4565277.2113 | 4665713.31 | 4768359.0028 | 4873262.9008 | 4980474.6847 | 5090045.1277 | 5202026.1205 | 5316470.6952 | 5433433.0505 | 5552968.5776 | 5675133.8863 | 5799986.8318 | 5927586.5421 | 6057993.446 | 6191269.3018 | 6327477.2265 | 6466681.7255 | 6608948.7234 | 6754345.5953 | 6902941.1984 | 7054805.9048 | 7210011.6347 | 7368631.8907 | 7530741.7923 | 7696418.1117 | 7865739.3101 | 8038785.575 | 8215638.8576 | 8396382.9125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3PH | OH | Value of avoided line losses |  | 46028.2337 | 46786.5502 | 45976.2434 | 46597.3271 | 47866.0613 | 48880.31 | 49857.9162 | 50855.0745 | 51872.176 | 52909.6195 | 54073.6311 | 55263.251 | 56479.0425 | 57721.5815 | 58991.4563 | 60289.2683 | 61615.6322 | 62971.1761 | 64356.542 | 65772.3859 | 67219.3784 | 68698.2047 | 70209.5652 | 71754.1757 | 73332.7675 | 74946.0884 | 76594.9024 | 78279.9902 | 80002.15 | 81762.1973 | 83560.9656 | 85399.3069 | 87278.0916 | 89198.2097 | 91160.5703 | 93166.1028 | 95215.7571 | 97310.5037 | 99451.3348 | 101639.2642 | 103875.328 | 106160.5852 | 108496.1181 | 110883.0327 | 113322.4594 | 115815.5535 | 118363.4957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 6345038.39 | 6484374.9299 | 6625191.5674 | 6770555.3882 | 6919751.1997 | 7071946.9215 | 7227431.9931 | 7386335.7811 | 7548733.4582 | 7714701.8499 | 7884425.2906 | 8057882.647 | 8235156.0652 | 8416329.4987 | 8601488.7476 | 8790721.5001 | 8984117.3731 | 9181767.9553 | 9383766.8503 | 9590209.721 | 9801194.3349 | 10016820.6103 | 10237190.6637 | 10462408.8583 | 10692581.8532 | 10927818.6539 | 11168230.6643 | 11413931.7389 | 11665038.2372 | 11921669.0784 | 12183945.7981 | 12451992.6057 | 12725936.443 | 13005907.0448 | 13292036.9998 | 13584461.8137 | 13883319.9737 | 14188753.0131 | 14500905.5794 | 14819925.5021 | 15145963.8632 | 15479175.0681 | 15819716.9196 | 16167750.6919 | 16523441.2071 | 16886956.9136 | 17258469.9657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
T&D Resilience Program - Underground (UG) - Project Type Detailed Annual Benefit Calcs
Phase | Type | Benefit Category | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090
1PH | UG | Customer Costs of Outages - Res |  | 17191.7747 | 17569.9937 | 17956.5336 | 18351.5773 | 18755.312 | 19167.9289 | 19589.6233 | 20020.595 | 20461.0481 | 20911.1912 | 21371.2374 | 21841.4046 | 22321.9155 | 22812.9977 | 23314.8836 | 23827.811 | 24352.0229 | 24887.7674 | 25435.2983 | 25994.8748 | 26566.7621 | 27151.2309 | 27748.5579 | 28359.0262 | 28982.9248 | 29620.5491 | 30272.2012 | 30938.1896 | 31618.8298 | 32314.4441 | 33025.3618 | 33751.9198 | 34494.462 | 35253.3402 | 36028.9137 | 36821.5498 | 37631.6239 | 38459.5196 | 39305.629 | 40170.3529 | 41054.1006 | 41957.2908 | 42880.3512 | 43823.719 | 44787.8408 | 45773.1733 | 46780.1831 | 47809.3471 | 48861.1528 | 49936.0981 | 51034.6923 | 52157.4555 | 53304.9195 | 54477.6278 | 55676.1356 | 56901.0106 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | Customer Costs of Outages - Nonres |  | 342254.2221 | 349783.8149 | 357479.0589 | 365343.5982 | 373381.1573 | 381595.5428 | 389990.6447 | 398570.4389 | 407338.9886 | 416300.4463 | 425459.0561 | 434819.1554 | 444385.1768 | 454161.6507 | 464153.207 | 474364.5776 | 484800.5983 | 495466.2114 | 506366.4681 | 517506.5304 | 528891.674 | 540527.2909 | 552418.8913 | 564572.1069 | 576992.6932 | 589686.5325 | 602659.6362 | 615918.1482 | 629468.3474 | 643316.6511 | 657469.6174 | 671933.949 | 686716.4959 | 701824.2588 | 717264.3925 | 733044.2091 | 749171.1817 | 765652.9477 | 782497.3126 | 799712.2534 | 817305.923 | 835286.6533 | 853662.9597 | 872443.5448 | 891637.3028 | 911253.3234 | 931300.8966 | 951789.5163 | 972728.8856 | 994128.9211 | 1015999.7574 | 1038351.7521 | 1061195.4906 | 1084541.7914 | 1108401.7108 | 1132786.5484 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | Feeder Backup - Customer Costs of Outages - Res |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | Feeder Backup - Customer Costs of Outages - Nonres |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1PH | UG | Value of avoided line losses |  | 10282.0275 | 10451.4242 | 10270.4136 | 10409.1546 | 10692.571 | 10919.1392 | 11137.522 | 11360.2724 | 11587.4779 | 11819.2274 | 12079.2504 | 12344.994 | 12616.5838 | 12894.1487 | 13177.8199 | 13467.732 | 13764.0221 | 14066.8306 | 14376.3008 | 14692.5795 | 15015.8162 | 15346.1642 | 15683.7798 | 16028.8229 | 16381.457 | 16741.8491 | 17110.1698 | 17486.5935 | 17871.2986 | 18264.4671 | 18666.2854 | 19076.9437 | 19496.6364 | 19925.5624 | 20363.9248 | 20811.9312 | 21269.7937 | 21737.7291 | 22215.9592 | 22704.7103 | 23204.2139 | 23714.7066 | 24236.4301 | 24769.6316 | 25314.5635 | 25871.4839 | 26440.6565 | 27022.351 | 27616.8427 | 28224.4132 | 28845.3503 | 29479.948 | 30128.5069 | 30791.334 | 31468.7434 | 32161.0557 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 369728.0243 | 377805.2329 | 385706.0061 | 394104.3301 | 402829.0404 | 411682.6109 | 420717.7901 | 429951.3064 | 439387.5146 | 449030.865 | 458909.544 | 469005.5539 | 479323.6761 | 489868.797 | 500645.9105 | 511660.1206 | 522916.6432 | 534420.8094 | 546178.0672 | 558193.9847 | 570474.2523 | 583024.6859 | 595851.229 | 608959.956 | 622357.075 | 636048.9307 | 650042.0072 | 664342.9313 | 678958.4758 | 693895.5623 | 709161.2646 | 724762.8125 | 740707.5943 | 757003.1614 | 773657.231 | 790677.6901 | 808072.5992 | 825850.1964 | 844018.9007 | 862587.3166 | 881564.2375 | 900958.6507 | 920779.7411 | 941036.8954 | 961739.7071 | 982897.9806 | 1004521.7362 | 1026621.2144 | 1049206.8811 | 1072289.4325 | 1095879.8 | 1119989.1556 | 1144628.917 | 1169810.7532 | 1195546.5898 | 1221848.6147 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Integrated Energy Storage Pilot - Program Detailed Annual Benefit Calcs
|  | Benefit / Cost Category | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090
Utility Costs
|  | Total Equipment & Installation Costs | 2027: 591280.5981; 2028: 839770.4919; 2029: 769357.9059; 2030: 709315.1931; 2031: 658184.1722; 2032: 611809.4148; 2033: 572569.0527; 2034: 539036.2069; 2035: 507130.24; 2036: 475324.2732; 2037: 443318.3064; 2038: 411212.3396; 2039: 379306.3728; 2040: 347300.406; 2041: 315194.4392; 2042: 283088.4723; 2043: 90795.4945; 2044: 2.4835e-11; 2045: 1.2017e-11; 2046: 1.2017e-11; 2047: 1.2017e-11; 2048: 1.2017e-11
|  | End of life Removal | 2027: 0; 2028: 0; 2029: 0; 2030: 0; 2031: 0; 2032: 0; 2033: 0; 2034: 0; 2035: 0; 2036: 0; 2037: 600; 2038: 900; 2039: 900; 2040: 2100; 2041: 2700; 2042: 3900; 2043: 8100; 2044: 15300; 2045: 21000; 2046: 25500; 2047: 9000; 2048: 0
|  | O&M | 2027: 600; 2028: 918; 2029: 936.36; 2030: 955.0872; 2031: 974.1889; 2032: 993.6727; 2033: 1013.5462; 2034: 1033.8171; 2035: 1054.4934; 2036: 1075.5833; 2037: 1089.781; 2038: 1100.3863; 2039: 1110.9798; 2040: 1106.0337; 2041: 1092.5284; 2042: 1061.8901; 2043: 971.9323; 2044: 777.134; 2045: 492.745; 2046: 131.113; 2047: 0; 2048: 0
|  | Software Fees | 2027: 0; 2028: 7200; 2029: 7200; 2030: 7200; 2031: 7200; 2032: 7200; 2033: 7200; 2034: 7200; 2035: 7200; 2036: 7200; 2037: 7152; 2038: 7080; 2039: 7008; 2040: 6840; 2041: 6624; 2042: 6312; 2043: 5664; 2044: 4440; 2045: 2760; 2046: 720; 2047: 0; 2048: 0
|  | RTE Credit | 2027: 13489.7927; 2028: 20639.3829; 2029: 20778.0907; 2030: 21053.8717; 2031: 21474.9492; 2032: 21904.4482; 2033: 22048.7871; 2034: 22339.9504; 2035: 22484.1729; 2036: 22779.5423; 2037: 22773.2146; 2038: 22686.5258; 2039: 22827.5502; 2040: 22410.3179; 2041: 21816.5817; 2042: 21115.9031; 2043: 19005.8323; 2044: 15129.3444; 2045: 9495.29; 2046: 2494.5571; 2047: 0; 2048: 0
|  | Total Costs | 2027: 605370.3908; 2028: 868527.8748; 2029: 798272.3566; 2030: 738524.152; 2031: 687833.3103; 2032: 641907.5357; 2033: 602831.386; 2034: 569609.9743; 2035: 537868.9063; 2036: 506379.3988; 2037: 474933.3021; 2038: 442979.2517; 2039: 411152.9028; 2040: 379756.7575; 2041: 347427.5492; 2042: 315478.2656; 2043: 124537.2591; 2044: 35646.4784; 2045: 33748.0349; 2046: 28845.6701; 2047: 9000; 2048: 1.2017e-11
Utility Avoided System Costs / revenues
|  | Energy | 2027: 27420.0635; 2028: 42654.0623; 2029: 42322.6782; 2030: 42276.3258; 2031: 43215.9444; 2032: 44214.2496; 2033: 45319.625; 2034: 46114.1611; 2035: 46629.3238; 2036: 47406.7443; 2037: 47732.2571; 2038: 47745.4988; 2039: 48063.9543; 2040: 47553.0224; 2041: 46831.1119; 2042: 45566.7603; 2043: 41471.1795; 2044: 33510.7613; 2045: 21804.2701; 2046: 7063.9436; 2047: 591.7239; 2048: 0
|  | DASI | 2027: 1285.2; 2028: 1966.356; 2029: 1992.9486; 2030: 2026.313; 2031: 2066.8393; 2032: 2108.176; 2033: 2136.5553; 2034: 2172.2565; 2035: 2201.3605; 2036: 2238.0738; 2037: 2252.9942; 2038: 2252.3974; 2039: 2266.3988; 2040: 2240.4749; 2041: 2204.5323; 2042: 2141.5457; 2043: 1940.7346; 2044: 1551.0754; 2045: 978.9771; 2046: 258.5548; 2047: 0; 2048: 0
|  | Rate 1 | 2027: 13489.7927; 2028: 20639.3829; 2029: 20778.0907; 2030: 21053.8717; 2031: 21474.9492; 2032: 21904.4482; 2033: 22048.7871; 2034: 22339.9504; 2035: 22484.1729; 2036: 22779.5423; 2037: 22773.2146; 2038: 22686.5258; 2039: 22827.5502; 2040: 22410.3179; 2041: 21816.5817; 2042: 21115.9031; 2043: 19005.8323; 2044: 15129.3444; 2045: 9495.29; 2046: 2494.5571; 2047: 0; 2048: 0
|  | Frequency | 2027: 38211.9413; 2028: 48720.2251; 2029: 41149.2568; 2030: 34865.1211; 2031: 29635.3529; 2032: 25190.05; 2033: 7137.1808; 2034: 0; 2035: 0; 2036: 0; 2037: 0; 2038: 0; 2039: 0; 2040: 0; 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0; 2047: 0; 2048: 0
|  | T&D Deferral | 2027: 0; 2028: 0; 2029: 0; 2030: 0; 2031: 0; 2032: 0; 2033: 149350; 2034: 224025; 2035: 74675; 2036: 0; 2037: 0; 2038: 0; 2039: 0; 2040: 0; 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0; 2047: 0; 2048: 0
|  | Power Factor/VAR support | 2027: 0; 2028: 0; 2029: 0; 2030: 0; 2031: 0; 2032: 0; 2033: 0; 2034: 0; 2035: 0; 2036: 0; 2037: 0; 2038: 0; 2039: 0; 2040: 0; 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0; 2047: 0; 2048: 0
|  | Capacity | 2027: 64434; 2028: 100240; 2029: 155334; 2030: 184674; 2031: 188880; 2032: 186609; 2033: 189109; 2034: 188552; 2035: 185973; 2036: 189719; 2037: 230694; 2038: 256090; 2039: 253922; 2040: 248434; 2041: 236317; 2042: 219753; 2043: 195379; 2044: 157426; 2045: 106461; 2046: 46472; 2047: 8505; 2048: 0
|  | RNS | 2027: 248622; 2028: 391174; 2029: 396312; 2030: 388903; 2031: 375483; 2032: 359319; 2033: 341926; 2034: 326224; 2035: 310248; 2036: 295941; 2037: 279853; 2038: 262650; 2039: 247852; 2040: 230291; 2041: 212798; 2042: 194121; 2043: 166194; 2044: 126168; 2045: 76794; 2046: 22426; 2047: 1442; 2048: 0
|  | Total Avoided System Costs | 2027: 393462.9975; 2028: 605394.0263; 2029: 657888.9743; 2030: 673798.6316; 2031: 660756.0858; 2032: 639344.9238; 2033: 757027.1483; 2034: 809427.368; 2035: 642210.8572; 2036: 558084.3603; 2037: 583305.466; 2038: 591424.4221; 2039: 574931.9033; 2040: 550928.8152; 2041: 519967.2259; 2042: 482698.2091; 2043: 423990.7464; 2044: 333785.1811; 2045: 215533.5372; 2046: 78715.0555; 2047: 10538.7239; 2048: 0
|  | Tier 3 value | 2027: 97000; 2028: 48500; 2029: 0
|  | Total Revenue | 2027: 490462.9975; 2028: 653894.0263; 2029: 657888.9743; 2030: 673798.6316; 2031: 660756.0858; 2032: 639344.9238; 2033: 757027.1483; 2034: 809427.368; 2035: 642210.8572; 2036: 558084.3603; 2037: 583305.466; 2038: 591424.4221; 2039: 574931.9033; 2040: 550928.8152; 2041: 519967.2259; 2042: 482698.2091; 2043: 423990.7464; 2044: 333785.1811; 2045: 215533.5372; 2046: 78715.0555; 2047: 10538.7239; 2048: 0
Customer Resilience Benefits
|  | Customer resilience value from reduced outages | 2027: 5382.3859; 2028: 8073.5789; 2029: 8235.0504; 2030: 8399.7514; 2031: 8567.7465; 2032: 8739.1014; 2033: 8913.8834; 2034: 9092.1611; 2035: 9274.0043; 2036: 9459.4844; 2037: 9648.6741; 2038: 9841.6476; 2039: 10038.4805; 2040: 10239.2501; 2041: 10444.0351; 2042: 10652.9158; 2043: 10865.9742; 2044: 11083.2936; 2045: 11304.9595; 2046: 11531.0587; 2047: 11761.6799
|  | Total Benefits | 495845.3834 | 661967.6052 | 666124.0247 | 682198.3831 | 669323.8323 | 648084.0252 | 765941.0317 | 818519.5291 | 651484.8615 | 567543.8447 | 592954.14 | 601266.0696 | 584970.3838 | 561168.0653 | 530411.261 | 493351.1249 | 434856.7206 | 344868.4748 | 226838.4967 | 90246.1142 | 22300.4038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Integrated Energy Storage Pilot - NPV cost and benefit summary
|  |  | WACC | Cost category | NPV Cost
|  |  | 6.46% | Total Equipment & Installation Costs | 5614596.5995
|  |  | 6.46% | End of life Removal | 28341.4307
|  |  | 6.46% | O&M | 10355.1952
|  |  | 6.46% | Software Fees | 67326.9434
|  |  | 6.46% | RTE Credit | 220926.0001
|  |  | 6.46% | Total NPV Costs | 5941546.1689
|  |  |  | Benefit Category | NPV Benefits
|  |  | 6.46% | Energy | 459063.7424
|  |  | 6.46% | DASI | 21599.9585
|  |  | 6.46% | Rate 1 | 220926.0001
|  |  | 6.46% | Frequency | 183704.5778
|  |  | 6.46% | T&D Deferral | 274641.5992
|  |  | 6.46% | Capacity | 1923548.7182
|  |  | 6.46% | RNS | 3237562.8171
|  |  | 6.46% | Tier 3 value | 133906.6473
|  |  |  | Total NPV Benefits | 6454954.0606

## Rev Req't_Baseline_OH1PH
Assumptions | Value |  |  | Baseline T&D Capital spent on target circuits
Equipment Life flag | 47 |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Book life flag | 50 |  |  | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037
MACRS flag | 20 |  | Unescalated Baseline Costs (from Construction, with Overheads) |  | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1
|  |  | Miles unescalated |  | 1.995 | 1.995 | 1.995 | 1.995 | 1.995 | 1.995 | 1.995 | 1.995 | 1.995 | 1.995
|  |  | Cost per mile unescalated |  | 502821.604 | 502821.604 | 502821.604 | 502821.604 | 502821.604 | 502821.604 | 502821.604 | 502821.604 | 502821.604 | 502821.604
|  |  | CPI |  | 1 | 1.022 | 1.0445 | 1.0675 | 1.0909 | 1.1149 | 1.1395 | 1.1645 | 1.1902 | 1.2163
|  |  | Escalated with CPI |  | 1003129.1 | 1025197.9402 | 1047752.2949 | 1070802.8454 | 1094360.508 | 1118436.4391 | 1143042.0408 | 1168188.9657 | 1193889.1229 | 1220154.6837
|  |  | Cost per mile escalated |  | 502821.604 | 513883.6793 | 525189.1202 | 536743.2809 | 548551.6331 | 560619.769 | 572953.4039 | 585558.3788 | 598440.6631 | 611606.3577
|  | Investment year in service |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100
QAQC check |  | 2027 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
1003129.1 |  |  | Book depreciation |  | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 20062.582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 1003129.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation |  | -20062.582 | -40125.164 | -60187.746 | -80250.328 | -100312.91 | -120375.492 | -140438.074 | -160500.656 | -180563.238 | -200625.82 | -220688.402 | -240750.984 | -260813.566 | -280876.148 | -300938.73 | -321001.312 | -341063.894 | -361126.476 | -381189.058 | -401251.64 | -421314.222 | -441376.804 | -461439.386 | -481501.968 | -501564.55 | -521627.132 | -541689.714 | -561752.296 | -581814.878 | -601877.46 | -621940.042 | -642002.624 | -662065.206 | -682127.788 | -702190.37 | -722252.952 | -742315.534 | -762378.116 | -782440.698 | -802503.28 | -822565.862 | -842628.444 | -862691.026 | -882753.608 | -902816.19 | -922878.772 | -942941.354 | -963003.936 | -983066.518 | -1003129.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) |  | 1003129.1 | 983066.518 | 963003.936 | 942941.354 | 922878.772 | 902816.19 | 882753.608 | 862691.026 | 842628.444 | 822565.862 | 802503.28 | 782440.698 | 762378.116 | 742315.534 | 722252.952 | 702190.37 | 682127.788 | 662065.206 | 642002.624 | 621940.042 | 601877.46 | 581814.878 | 561752.296 | 541689.714 | 521627.132 | 501564.55 | 481501.968 | 461439.386 | 441376.804 | 421314.222 | 401251.64 | 381189.058 | 361126.476 | 341063.894 | 321001.312 | 300938.73 | 280876.148 | 260813.566 | 240750.984 | 220688.402 | 200625.82 | 180563.238 | 160500.656 | 140438.074 | 120375.492 | 100312.91 | 80250.328 | 60187.746 | 40125.164 | 20062.582 | -1.0477e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) | 1003129.1 | 983066.518 | 963003.936 | 942941.354 | 922878.772 | 902816.19 | 882753.608 | 862691.026 | 842628.444 | 822565.862 | 802503.28 | 782440.698 | 762378.116 | 742315.534 | 722252.952 | 702190.37 | 682127.788 | 662065.206 | 642002.624 | 621940.042 | 601877.46 | 581814.878 | 561752.296 | 541689.714 | 521627.132 | 501564.55 | 481501.968 | 461439.386 | 441376.804 | 421314.222 | 401251.64 | 381189.058 | 361126.476 | 341063.894 | 321001.312 | 300938.73 | 280876.148 | 260813.566 | 240750.984 | 220688.402 | 200625.82 | 180563.238 | 160500.656 | 140438.074 | 120375.492 | 100312.91 | 80250.328 | 60187.746 | 40125.164 | 20062.582 | -1.0477e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation |  | 37617.3413 | 72415.8897 | 66978.93 | 61963.2845 | 57308.7655 | 53015.3729 | 49032.9504 | 45361.4979 | 44759.6204 | 44749.5892 | 44759.6204 | 44749.5892 | 44759.6204 | 44749.5892 | 44759.6204 | 44749.5892 | 44759.6204 | 44749.5892 | 44759.6204 | 44749.5892 | 22379.8102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) |  | 0 | -4865.3015 | -19375.0208 | -32377.8866 | -43990.6663 | -54313.4461 | -63446.3121 | -71475.4497 | -78487.0442 | -85331.8284 | -92173.8325 | -99018.6167 | -105860.6207 | -112705.4049 | -119547.4089 | -126392.1931 | -133234.1972 | -140078.9814 | -146920.9854 | -153765.7696 | -160607.7736 | -161249.9934 | -155689.6488 | -150129.3042 | -144568.9596 | -139008.615 | -133448.2704 | -127887.9258 | -122327.5812 | -116767.2366 | -111206.892 | -105646.5474 | -100086.2028 | -94525.8582 | -88965.5136 | -83405.169 | -77844.8244 | -72284.4798 | -66724.1352 | -61163.7906 | -55603.446 | -50043.1014 | -44482.7568 | -38922.4122 | -33362.0676 | -27801.723 | -22241.3784 | -16681.0338 | -11120.6892 | -5560.3446 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11
|  |  | ADIT (e.o.y.) |  | -4865.3015 | -19375.0208 | -32377.8866 | -43990.6663 | -54313.4461 | -63446.3121 | -71475.4497 | -78487.0442 | -85331.8284 | -92173.8325 | -99018.6167 | -105860.6207 | -112705.4049 | -119547.4089 | -126392.1931 | -133234.1972 | -140078.9814 | -146920.9854 | -153765.7696 | -160607.7736 | -161249.9934 | -155689.6488 | -150129.3042 | -144568.9596 | -139008.615 | -133448.2704 | -127887.9258 | -122327.5812 | -116767.2366 | -111206.892 | -105646.5474 | -100086.2028 | -94525.8582 | -88965.5136 | -83405.169 | -77844.8244 | -72284.4798 | -66724.1352 | -61163.7906 | -55603.446 | -50043.1014 | -44482.7568 | -38922.4122 | -33362.0676 | -27801.723 | -22241.3784 | -16681.0338 | -11120.6892 | -5560.3446 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11
|  |  | Net Rate Base |  | 990665.1582 | 960915.0659 | 927096.1913 | 894725.7865 | 863695.4248 | 833905.0199 | 805261.4361 | 777678.4881 | 750687.7167 | 723781.7406 | 696875.7644 | 669969.7883 | 643063.8122 | 616157.8361 | 589251.86 | 562345.8839 | 535439.9077 | 508533.9316 | 481627.9555 | 454721.9794 | 430917.2855 | 413313.7659 | 398811.5285 | 384309.2911 | 369807.0537 | 355304.8163 | 340802.5789 | 326300.3415 | 311798.1041 | 297295.8667 | 282793.6293 | 268291.3919 | 253789.1545 | 239286.9171 | 224784.6797 | 210282.4423 | 195780.2049 | 181277.9675 | 166775.7301 | 152273.4927 | 137771.2553 | 123269.0179 | 108766.7805 | 94264.5431 | 79762.3057 | 65260.0683 | 50757.8309 | 36255.5935 | 21753.3561 | 7251.1187 | -4.602e-10 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11 | 6.3665e-11
|  |  | Pre-Tax return on rate base |  | 88466.3986 | 85809.7154 | 82789.6899 | 79899.0127 | 77128.0014 | 74467.7183 | 71909.8462 | 69446.689 | 67036.4131 | 64633.7094 | 62231.0058 | 59828.3021 | 57425.5984 | 55022.8948 | 52620.1911 | 50217.4874 | 47814.7838 | 45412.0801 | 43009.3764 | 40606.6728 | 38480.9136 | 36908.9193 | 35613.8695 | 34318.8197 | 33023.7699 | 31728.7201 | 30433.6703 | 29138.6205 | 27843.5707 | 26548.5209 | 25253.4711 | 23958.4213 | 22663.3715 | 21368.3217 | 20073.2719 | 18778.2221 | 17483.1723 | 16188.1225 | 14893.0727 | 13598.0229 | 12302.9731 | 11007.9233 | 9712.8735 | 8417.8237 | 7122.7739 | 5827.7241 | 4532.6743 | 3237.6245 | 1942.5747 | 647.5249 | -4.1096e-11 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12 | 5.6853e-12
|  | Investment year in service |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99
QAQC check |  | 2028 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
1025197.9402 |  |  | Book depreciation |  |  | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 20503.9588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service |  | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 1025197.9402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation |  |  | -20503.9588 | -41007.9176 | -61511.8764 | -82015.8352 | -102519.794 | -123023.7528 | -143527.7116 | -164031.6704 | -184535.6292 | -205039.588 | -225543.5468 | -246047.5056 | -266551.4645 | -287055.4233 | -307559.3821 | -328063.3409 | -348567.2997 | -369071.2585 | -389575.2173 | -410079.1761 | -430583.1349 | -451087.0937 | -471591.0525 | -492095.0113 | -512598.9701 | -533102.9289 | -553606.8877 | -574110.8465 | -594614.8053 | -615118.7641 | -635622.7229 | -656126.6817 | -676630.6405 | -697134.5993 | -717638.5581 | -738142.5169 | -758646.4757 | -779150.4346 | -799654.3934 | -820158.3522 | -840662.311 | -861166.2698 | -881670.2286 | -902174.1874 | -922678.1462 | -943182.105 | -963686.0638 | -984190.0226 | -1004693.9814 | -1025197.9402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) |  |  | 1025197.9402 | 1004693.9814 | 984190.0226 | 963686.0638 | 943182.105 | 922678.1462 | 902174.1874 | 881670.2286 | 861166.2698 | 840662.311 | 820158.3522 | 799654.3934 | 779150.4346 | 758646.4757 | 738142.5169 | 717638.5581 | 697134.5993 | 676630.6405 | 656126.6817 | 635622.7229 | 615118.7641 | 594614.8053 | 574110.8465 | 553606.8877 | 533102.9289 | 512598.9701 | 492095.0113 | 471591.0525 | 451087.0937 | 430583.1349 | 410079.1761 | 389575.2173 | 369071.2585 | 348567.2997 | 328063.3409 | 307559.3821 | 287055.4233 | 266551.4645 | 246047.5056 | 225543.5468 | 205039.588 | 184535.6292 | 164031.6704 | 143527.7116 | 123023.7528 | 102519.794 | 82015.8352 | 61511.8764 | 41007.9176 | 20503.9588 | -1.1642e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) |  | 1025197.9402 | 1004693.9814 | 984190.0226 | 963686.0638 | 943182.105 | 922678.1462 | 902174.1874 | 881670.2286 | 861166.2698 | 840662.311 | 820158.3522 | 799654.3934 | 779150.4346 | 758646.4757 | 738142.5169 | 717638.5581 | 697134.5993 | 676630.6405 | 656126.6817 | 635622.7229 | 615118.7641 | 594614.8053 | 574110.8465 | 553606.8877 | 533102.9289 | 512598.9701 | 492095.0113 | 471591.0525 | 451087.0937 | 430583.1349 | 410079.1761 | 389575.2173 | 369071.2585 | 348567.2997 | 328063.3409 | 307559.3821 | 287055.4233 | 266551.4645 | 246047.5056 | 225543.5468 | 205039.588 | 184535.6292 | 164031.6704 | 143527.7116 | 123023.7528 | 102519.794 | 82015.8352 | 61511.8764 | 41007.9176 | 20503.9588 | -1.1642e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation |  |  | 38444.9228 | 74009.0393 | 68452.4665 | 63326.4768 | 58569.5583 | 54181.7111 | 50111.6753 | 46359.4509 | 45744.3321 | 45734.0801 | 45744.3321 | 45734.0801 | 45744.3321 | 45734.0801 | 45744.3321 | 45734.0801 | 45744.3321 | 45734.0801 | 45744.3321 | 45734.0801 | 22872.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) |  |  | 0 | -4972.3382 | -19801.2712 | -33090.2001 | -44958.461 | -55508.3419 | -64842.1309 | -73047.9096 | -80213.7592 | -87209.1286 | -94201.6568 | -101197.0262 | -108189.5543 | -115184.9238 | -122177.4519 | -129172.8214 | -136165.3495 | -143160.719 | -150153.2471 | -157148.6165 | -164141.1447 | -164797.4933 | -159114.8211 | -153432.1489 | -147749.4767 | -142066.8046 | -136384.1324 | -130701.4602 | -125018.788 | -119336.1158 | -113653.4437 | -107970.7715 | -102288.0993 | -96605.4271 | -90922.7549 | -85240.0827 | -79557.4106 | -73874.7384 | -68192.0662 | -62509.394 | -56826.7218 | -51144.0496 | -45461.3775 | -39778.7053 | -34096.0331 | -28413.3609 | -22730.6887 | -17048.0165 | -11365.3444 | -5682.6722 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10
|  |  | ADIT (e.o.y.) |  |  | -4972.3382 | -19801.2712 | -33090.2001 | -44958.461 | -55508.3419 | -64842.1309 | -73047.9096 | -80213.7592 | -87209.1286 | -94201.6568 | -101197.0262 | -108189.5543 | -115184.9238 | -122177.4519 | -129172.8214 | -136165.3495 | -143160.719 | -150153.2471 | -157148.6165 | -164141.1447 | -164797.4933 | -159114.8211 | -153432.1489 | -147749.4767 | -142066.8046 | -136384.1324 | -130701.4602 | -125018.788 | -119336.1158 | -113653.4437 | -107970.7715 | -102288.0993 | -96605.4271 | -90922.7549 | -85240.0827 | -79557.4106 | -73874.7384 | -68192.0662 | -62509.394 | -56826.7218 | -51144.0496 | -45461.3775 | -39778.7053 | -34096.0331 | -28413.3609 | -22730.6887 | -17048.0165 | -11365.3444 | -5682.6722 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10
|  |  | Net Rate Base |  |  | 1012459.7917 | 982055.1973 | 947492.3075 | 914409.7538 | 882696.7242 | 852250.9304 | 822977.1877 | 794787.4148 | 767202.8464 | 739704.9389 | 712207.0313 | 684709.1237 | 657211.2161 | 629713.3085 | 602215.4009 | 574717.4933 | 547219.5857 | 519721.6781 | 492223.7705 | 464725.8629 | 440397.4657 | 422406.6687 | 407585.3821 | 392764.0955 | 377942.8088 | 363121.5222 | 348300.2356 | 333478.949 | 318657.6624 | 303836.3757 | 289015.0891 | 274193.8025 | 259372.5159 | 244551.2293 | 229729.9426 | 214908.656 | 200087.3694 | 185266.0828 | 170444.7961 | 155623.5095 | 140802.2229 | 125980.9363 | 111159.6497 | 96338.363 | 81517.0764 | 66695.7898 | 51874.5032 | 37053.2166 | 22231.9299 | 7410.6433 | -6.9849e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10
|  |  | Pre-Tax return on rate base |  |  | 90412.6594 | 87697.5291 | 84611.0631 | 81656.791 | 78824.8175 | 76106.0081 | 73491.8629 | 70974.5161 | 68511.2142 | 66055.651 | 63600.0879 | 61144.5247 | 58688.9616 | 56233.3984 | 53777.8353 | 51322.2722 | 48866.709 | 46411.1459 | 43955.5827 | 41500.0196 | 39327.4937 | 37720.9155 | 36397.3746 | 35073.8337 | 33750.2928 | 32426.7519 | 31103.211 | 29779.6701 | 28456.1292 | 27132.5884 | 25809.0475 | 24485.5066 | 23161.9657 | 21838.4248 | 20514.8839 | 19191.343 | 17867.8021 | 16544.2612 | 15220.7203 | 13897.1794 | 12573.6385 | 11250.0976 | 9926.5567 | 8603.0158 | 7279.4749 | 5955.934 | 4632.3931 | 3308.8522 | 1985.3113 | 661.7704 | -6.2375e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11
|  | Investment year in service |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98
QAQC check |  | 2029 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
1047752.2949 |  |  | Book depreciation |  |  |  | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 20955.0459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service |  |  | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 1047752.2949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation |  |  |  | -20955.0459 | -41910.0918 | -62865.1377 | -83820.1836 | -104775.2295 | -125730.2754 | -146685.3213 | -167640.3672 | -188595.4131 | -209550.459 | -230505.5049 | -251460.5508 | -272415.5967 | -293370.6426 | -314325.6885 | -335280.7344 | -356235.7803 | -377190.8262 | -398145.8721 | -419100.918 | -440055.9639 | -461011.0097 | -481966.0556 | -502921.1015 | -523876.1474 | -544831.1933 | -565786.2392 | -586741.2851 | -607696.331 | -628651.3769 | -649606.4228 | -670561.4687 | -691516.5146 | -712471.5605 | -733426.6064 | -754381.6523 | -775336.6982 | -796291.7441 | -817246.79 | -838201.8359 | -859156.8818 | -880111.9277 | -901066.9736 | -922022.0195 | -942977.0654 | -963932.1113 | -984887.1572 | -1005842.2031 | -1026797.249 | -1047752.2949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) |  |  |  | 1047752.2949 | 1026797.249 | 1005842.2031 | 984887.1572 | 963932.1113 | 942977.0654 | 922022.0195 | 901066.9736 | 880111.9277 | 859156.8818 | 838201.8359 | 817246.79 | 796291.7441 | 775336.6982 | 754381.6523 | 733426.6064 | 712471.5605 | 691516.5146 | 670561.4687 | 649606.4228 | 628651.3769 | 607696.331 | 586741.2851 | 565786.2392 | 544831.1933 | 523876.1474 | 502921.1015 | 481966.0556 | 461011.0097 | 440055.9639 | 419100.918 | 398145.8721 | 377190.8262 | 356235.7803 | 335280.7344 | 314325.6885 | 293370.6426 | 272415.5967 | 251460.5508 | 230505.5049 | 209550.459 | 188595.4131 | 167640.3672 | 146685.3213 | 125730.2754 | 104775.2295 | 83820.1836 | 62865.1377 | 41910.0918 | 20955.0459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) |  |  | 1047752.2949 | 1026797.249 | 1005842.2031 | 984887.1572 | 963932.1113 | 942977.0654 | 922022.0195 | 901066.9736 | 880111.9277 | 859156.8818 | 838201.8359 | 817246.79 | 796291.7441 | 775336.6982 | 754381.6523 | 733426.6064 | 712471.5605 | 691516.5146 | 670561.4687 | 649606.4228 | 628651.3769 | 607696.331 | 586741.2851 | 565786.2392 | 544831.1933 | 523876.1474 | 502921.1015 | 481966.0556 | 461011.0097 | 440055.9639 | 419100.918 | 398145.8721 | 377190.8262 | 356235.7803 | 335280.7344 | 314325.6885 | 293370.6426 | 272415.5967 | 251460.5508 | 230505.5049 | 209550.459 | 188595.4131 | 167640.3672 | 146685.3213 | 125730.2754 | 104775.2295 | 83820.1836 | 62865.1377 | 41910.0918 | 20955.0459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation |  |  |  | 39290.7111 | 75637.2382 | 69958.4207 | 64719.6593 | 59858.0886 | 55373.7088 | 51214.1322 | 47379.3588 | 46750.7074 | 46740.2299 | 46750.7074 | 46740.2299 | 46750.7074 | 46740.2299 | 46750.7074 | 46740.2299 | 46750.7074 | 46740.2299 | 46750.7074 | 46740.2299 | 23375.3537 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) |  |  |  | 0 | -5081.7296 | -20236.8992 | -33818.1845 | -45947.5471 | -56729.5254 | -66268.6578 | -74654.9636 | -81978.4619 | -89127.7295 | -96274.0932 | -103423.3608 | -110569.7245 | -117718.9921 | -124865.3559 | -132014.6235 | -139160.9872 | -146310.2548 | -153456.6185 | -160605.8861 | -167752.2498 | -168423.0381 | -162615.3472 | -156807.6562 | -150999.9652 | -145192.2743 | -139384.5833 | -133576.8923 | -127769.2014 | -121961.5104 | -116153.8194 | -110346.1284 | -104538.4375 | -98730.7465 | -92923.0555 | -87115.3646 | -81307.6736 | -75499.9826 | -69692.2916 | -63884.6007 | -58076.9097 | -52269.2187 | -46461.5278 | -40653.8368 | -34846.1458 | -29038.4549 | -23230.7639 | -17423.0729 | -11615.3819 | -5807.691 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11
|  |  | ADIT (e.o.y.) |  |  |  | -5081.7296 | -20236.8992 | -33818.1845 | -45947.5471 | -56729.5254 | -66268.6578 | -74654.9636 | -81978.4619 | -89127.7295 | -96274.0932 | -103423.3608 | -110569.7245 | -117718.9921 | -124865.3559 | -132014.6235 | -139160.9872 | -146310.2548 | -153456.6185 | -160605.8861 | -167752.2498 | -168423.0381 | -162615.3472 | -156807.6562 | -150999.9652 | -145192.2743 | -139384.5833 | -133576.8923 | -127769.2014 | -121961.5104 | -116153.8194 | -110346.1284 | -104538.4375 | -98730.7465 | -92923.0555 | -87115.3646 | -81307.6736 | -75499.9826 | -69692.2916 | -63884.6007 | -58076.9097 | -52269.2187 | -46461.5278 | -40653.8368 | -34846.1458 | -29038.4549 | -23230.7639 | -17423.0729 | -11615.3819 | -5807.691 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11
|  |  | Net Rate Base |  |  |  | 1034733.9071 | 1003660.4116 | 968337.1383 | 934526.7684 | 902116.0521 | 871000.4508 | 841082.6858 | 812272.7379 | 784081.3091 | 755978.4475 | 727875.5859 | 699772.7244 | 671669.8628 | 643567.0013 | 615464.1397 | 587361.2781 | 559258.4166 | 531155.555 | 503052.6935 | 474949.8319 | 450086.21 | 431699.6154 | 416552.2605 | 401404.9056 | 386257.5506 | 371110.1957 | 355962.8408 | 340815.4859 | 325668.1309 | 310520.776 | 295373.4211 | 280226.0662 | 265078.7112 | 249931.3563 | 234784.0014 | 219636.6464 | 204489.2915 | 189341.9366 | 174194.5817 | 159047.2267 | 143899.8718 | 128752.5169 | 113605.162 | 98457.807 | 83310.4521 | 68163.0972 | 53015.7422 | 37868.3873 | 22721.0324 | 7573.6775 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11 | 8.7311e-11
|  |  | Pre-Tax return on rate base |  |  |  | 92401.7379 | 89626.8748 | 86472.5064 | 83453.2404 | 80558.9635 | 77780.3403 | 75108.6838 | 72535.9555 | 70018.4609 | 67508.8754 | 64999.2898 | 62489.7043 | 59980.1188 | 57470.5332 | 54960.9477 | 52451.3621 | 49941.7766 | 47432.1911 | 44922.6055 | 42413.02 | 40192.6986 | 38550.7757 | 37198.1169 | 35845.4581 | 34492.7993 | 33140.1405 | 31787.4817 | 30434.8229 | 29082.1641 | 27729.5053 | 26376.8465 | 25024.1877 | 23671.5289 | 22318.8701 | 20966.2113 | 19613.5525 | 18260.8937 | 16908.2349 | 15555.5761 | 14202.9173 | 12850.2586 | 11497.5998 | 10144.941 | 8792.2822 | 7439.6234 | 6086.9646 | 4734.3058 | 3381.647 | 2028.9882 | 676.3294 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12 | 7.7969e-12
|  | Investment year in service |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97
|  | 2030 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
|  |  | Book depreciation |  |  |  |  | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 21416.0569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service |  |  |  | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 1070802.8454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation |  |  |  |  | -21416.0569 | -42832.1138 | -64248.1707 | -85664.2276 | -107080.2845 | -128496.3414 | -149912.3984 | -171328.4553 | -192744.5122 | -214160.5691 | -235576.626 | -256992.6829 | -278408.7398 | -299824.7967 | -321240.8536 | -342656.9105 | -364072.9674 | -385489.0243 | -406905.0812 | -428321.1381 | -449737.1951 | -471153.252 | -492569.3089 | -513985.3658 | -535401.4227 | -556817.4796 | -578233.5365 | -599649.5934 | -621065.6503 | -642481.7072 | -663897.7641 | -685313.821 | -706729.8779 | -728145.9349 | -749561.9918 | -770978.0487 | -792394.1056 | -813810.1625 | -835226.2194 | -856642.2763 | -878058.3332 | -899474.3901 | -920890.447 | -942306.5039 | -963722.5608 | -985138.6177 | -1006554.6746 | -1027970.7316 | -1049386.7885 | -1070802.8454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) |  |  |  |  | 1070802.8454 | 1049386.7885 | 1027970.7316 | 1006554.6746 | 985138.6177 | 963722.5608 | 942306.5039 | 920890.447 | 899474.3901 | 878058.3332 | 856642.2763 | 835226.2194 | 813810.1625 | 792394.1056 | 770978.0487 | 749561.9918 | 728145.9349 | 706729.8779 | 685313.821 | 663897.7641 | 642481.7072 | 621065.6503 | 599649.5934 | 578233.5365 | 556817.4796 | 535401.4227 | 513985.3658 | 492569.3089 | 471153.252 | 449737.1951 | 428321.1381 | 406905.0812 | 385489.0243 | 364072.9674 | 342656.9105 | 321240.8536 | 299824.7967 | 278408.7398 | 256992.6829 | 235576.626 | 214160.5691 | 192744.5122 | 171328.4553 | 149912.3984 | 128496.3414 | 107080.2845 | 85664.2276 | 64248.1707 | 42832.1138 | 21416.0569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) |  |  |  | 1070802.8454 | 1049386.7885 | 1027970.7316 | 1006554.6746 | 985138.6177 | 963722.5608 | 942306.5039 | 920890.447 | 899474.3901 | 878058.3332 | 856642.2763 | 835226.2194 | 813810.1625 | 792394.1056 | 770978.0487 | 749561.9918 | 728145.9349 | 706729.8779 | 685313.821 | 663897.7641 | 642481.7072 | 621065.6503 | 599649.5934 | 578233.5365 | 556817.4796 | 535401.4227 | 513985.3658 | 492569.3089 | 471153.252 | 449737.1951 | 428321.1381 | 406905.0812 | 385489.0243 | 364072.9674 | 342656.9105 | 321240.8536 | 299824.7967 | 278408.7398 | 256992.6829 | 235576.626 | 214160.5691 | 192744.5122 | 171328.4553 | 149912.3984 | 128496.3414 | 107080.2845 | 85664.2276 | 64248.1707 | 42832.1138 | 21416.0569 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation |  |  |  |  | 40155.1067 | 77301.2574 | 71497.506 | 66143.4918 | 61174.9666 | 56591.9304 | 52340.8431 | 48421.7047 | 47779.223 | 47768.5149 | 47779.223 | 47768.5149 | 47779.223 | 47768.5149 | 47779.223 | 47768.5149 | 47779.223 | 47768.5149 | 47779.223 | 47768.5149 | 23889.6115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) |  |  |  |  | 0 | -5193.5277 | -20682.111 | -34562.1846 | -46958.3931 | -57977.575 | -67726.5683 | -76297.3728 | -83781.9881 | -91088.5395 | -98392.1233 | -105698.6747 | -113002.2585 | -120308.81 | -127612.3937 | -134918.9452 | -142222.5289 | -149529.0804 | -156832.6641 | -164139.2156 | -171442.7993 | -172128.345 | -166192.8848 | -160257.4246 | -154321.9645 | -148386.5043 | -142451.0441 | -136515.584 | -130580.1238 | -124644.6636 | -118709.2034 | -112773.7433 | -106838.2831 | -100902.8229 | -94967.3628 | -89031.9026 | -83096.4424 | -77160.9822 | -71225.5221 | -65290.0619 | -59354.6017 | -53419.1415 | -47483.6814 | -41548.2212 | -35612.761 | -29677.3009 | -23741.8407 | -17806.3805 | -11870.9203 | -5935.4602 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11
|  |  | ADIT (e.o.y.) |  |  |  |  | -5193.5277 | -20682.111 | -34562.1846 | -46958.3931 | -57977.575 | -67726.5683 | -76297.3728 | -83781.9881 | -91088.5395 | -98392.1233 | -105698.6747 | -113002.2585 | -120308.81 | -127612.3937 | -134918.9452 | -142222.5289 | -149529.0804 | -156832.6641 | -164139.2156 | -171442.7993 | -172128.345 | -166192.8848 | -160257.4246 | -154321.9645 | -148386.5043 | -142451.0441 | -136515.584 | -130580.1238 | -124644.6636 | -118709.2034 | -112773.7433 | -106838.2831 | -100902.8229 | -94967.3628 | -89031.9026 | -83096.4424 | -77160.9822 | -71225.5221 | -65290.0619 | -59354.6017 | -53419.1415 | -47483.6814 | -41548.2212 | -35612.761 | -29677.3009 | -23741.8407 | -17806.3805 | -11870.9203 | -5935.4602 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11
|  |  | Net Rate Base |  |  |  |  | 1057498.0531 | 1025740.9407 | 989640.5553 | 955086.3573 | 921962.6052 | 890162.4608 | 859586.5049 | 830142.7381 | 801331.0979 | 772609.9734 | 743888.8488 | 715167.7243 | 686446.5998 | 657725.4753 | 629004.3508 | 600283.2263 | 571562.1018 | 542840.9772 | 514119.8527 | 485398.7282 | 459988.1066 | 441197.007 | 425716.4102 | 410235.8135 | 394755.2168 | 379274.62 | 363794.0233 | 348313.4265 | 332832.8298 | 317352.2331 | 301871.6363 | 286391.0396 | 270910.4429 | 255429.8461 | 239949.2494 | 224468.6527 | 208988.0559 | 193507.4592 | 178026.8625 | 162546.2657 | 147065.669 | 131585.0723 | 116104.4755 | 100623.8788 | 85143.282 | 69662.6853 | 54182.0886 | 38701.4918 | 23220.8951 | 7740.2984 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11 | 4.9113e-11
|  |  | Pre-Tax return on rate base |  |  |  |  | 94434.5761 | 91598.666 | 88374.9016 | 85289.2117 | 82331.2606 | 79491.5077 | 76761.0749 | 74131.7465 | 71558.867 | 68994.0706 | 66429.2742 | 63864.4778 | 61299.6814 | 58734.8849 | 56170.0885 | 53605.2921 | 51040.4957 | 48475.6993 | 45910.9028 | 43346.1064 | 41076.9379 | 39398.8927 | 38016.4754 | 36634.0581 | 35251.6409 | 33869.2236 | 32486.8063 | 31104.389 | 29721.9717 | 28339.5544 | 26957.1371 | 25574.7198 | 24192.3025 | 22809.8853 | 21427.468 | 20045.0507 | 18662.6334 | 17280.2161 | 15897.7988 | 14515.3815 | 13132.9642 | 11750.547 | 10368.1297 | 8985.7124 | 7603.2951 | 6220.8778 | 4838.4605 | 3456.0432 | 2073.6259 | 691.2086 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12 | 4.3858e-12
|  | Investment year in service | [5 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96
|  | 2031 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
|  |  | Book depreciation | [5 empty] | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 21887.2102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service |  |  |  |  | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 1094360.508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation | [5 empty] | -21887.2102 | -43774.4203 | -65661.6305 | -87548.8406 | -109436.0508 | -131323.261 | -153210.4711 | -175097.6813 | -196984.8914 | -218872.1016 | -240759.3118 | -262646.5219 | -284533.7321 | -306420.9422 | -328308.1524 | -350195.3626 | -372082.5727 | -393969.7829 | -415856.993 | -437744.2032 | -459631.4133 | -481518.6235 | -503405.8337 | -525293.0438 | -547180.254 | -569067.4641 | -590954.6743 | -612841.8845 | -634729.0946 | -656616.3048 | -678503.5149 | -700390.7251 | -722277.9353 | -744165.1454 | -766052.3556 | -787939.5657 | -809826.7759 | -831713.9861 | -853601.1962 | -875488.4064 | -897375.6165 | -919262.8267 | -941150.0369 | -963037.247 | -984924.4572 | -1006811.6673 | -1028698.8775 | -1050586.0877 | -1072473.2978 | -1094360.508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) | [5 empty] | 1094360.508 | 1072473.2978 | 1050586.0877 | 1028698.8775 | 1006811.6673 | 984924.4572 | 963037.247 | 941150.0369 | 919262.8267 | 897375.6165 | 875488.4064 | 853601.1962 | 831713.9861 | 809826.7759 | 787939.5657 | 766052.3556 | 744165.1454 | 722277.9353 | 700390.7251 | 678503.5149 | 656616.3048 | 634729.0946 | 612841.8845 | 590954.6743 | 569067.4641 | 547180.254 | 525293.0438 | 503405.8337 | 481518.6235 | 459631.4133 | 437744.2032 | 415856.993 | 393969.7829 | 372082.5727 | 350195.3626 | 328308.1524 | 306420.9422 | 284533.7321 | 262646.5219 | 240759.3118 | 218872.1016 | 196984.8914 | 175097.6813 | 153210.4711 | 131323.261 | 109436.0508 | 87548.8406 | 65661.6305 | 43774.4203 | 21887.2102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) |  |  |  |  | 1094360.508 | 1072473.2978 | 1050586.0877 | 1028698.8775 | 1006811.6673 | 984924.4572 | 963037.247 | 941150.0369 | 919262.8267 | 897375.6165 | 875488.4064 | 853601.1962 | 831713.9861 | 809826.7759 | 787939.5657 | 766052.3556 | 744165.1454 | 722277.9353 | 700390.7251 | 678503.5149 | 656616.3048 | 634729.0946 | 612841.8845 | 590954.6743 | 569067.4641 | 547180.254 | 525293.0438 | 503405.8337 | 481518.6235 | 459631.4133 | 437744.2032 | 415856.993 | 393969.7829 | 372082.5727 | 350195.3626 | 328308.1524 | 306420.9422 | 284533.7321 | 262646.5219 | 240759.3118 | 218872.1016 | 196984.8914 | 175097.6813 | 153210.4711 | 131323.261 | 109436.0508 | 87548.8406 | 65661.6305 | 43774.4203 | 21887.2102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation | [5 empty] | 41038.519 | 79001.8851 | 73070.4511 | 67598.6486 | 62520.8158 | 57836.9528 | 53492.3416 | 49486.9822 | 48830.3659 | 48819.4223 | 48830.3659 | 48819.4223 | 48830.3659 | 48819.4223 | 48830.3659 | 48819.4223 | 48830.3659 | 48819.4223 | 48830.3659 | 48819.4223 | 24415.1829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) | [5 empty] | 0 | -5307.7853 | -21137.1174 | -35322.5526 | -47991.4778 | -59253.0816 | -69216.5528 | -77975.915 | -85625.1918 | -93092.4874 | -100556.75 | -108024.0456 | -115488.3082 | -122955.6038 | -130419.8664 | -137887.162 | -145351.4245 | -152818.7201 | -160282.9827 | -167750.2783 | -175214.5409 | -175915.1686 | -169849.1283 | -163783.088 | -157717.0477 | -151651.0074 | -145584.9671 | -139518.9268 | -133452.8865 | -127386.8462 | -121320.8059 | -115254.7656 | -109188.7253 | -103122.685 | -97056.6447 | -90990.6044 | -84924.5641 | -78858.5238 | -72792.4835 | -66726.4433 | -60660.403 | -54594.3627 | -48528.3224 | -42462.2821 | -36396.2418 | -30330.2015 | -24264.1612 | -18198.1209 | -12132.0806 | -6066.0403 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11
|  |  | ADIT (e.o.y.) | [5 empty] | -5307.7853 | -21137.1174 | -35322.5526 | -47991.4778 | -59253.0816 | -69216.5528 | -77975.915 | -85625.1918 | -93092.4874 | -100556.75 | -108024.0456 | -115488.3082 | -122955.6038 | -130419.8664 | -137887.162 | -145351.4245 | -152818.7201 | -160282.9827 | -167750.2783 | -175214.5409 | -175915.1686 | -169849.1283 | -163783.088 | -157717.0477 | -151651.0074 | -145584.9671 | -139518.9268 | -133452.8865 | -127386.8462 | -121320.8059 | -115254.7656 | -109188.7253 | -103122.685 | -97056.6447 | -90990.6044 | -84924.5641 | -78858.5238 | -72792.4835 | -66726.4433 | -60660.403 | -54594.3627 | -48528.3224 | -42462.2821 | -36396.2418 | -30330.2015 | -24264.1612 | -18198.1209 | -12132.0806 | -6066.0403 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11
|  |  | Net Rate Base | [5 empty] | 1080763.0103 | 1048307.2414 | 1011412.6475 | 976098.2572 | 942245.7825 | 909746.0349 | 878497.408 | 848405.8784 | 818960.382 | 789607.3928 | 760254.4035 | 730901.4143 | 701548.425 | 672195.4358 | 642842.4465 | 613489.4572 | 584136.468 | 554783.4787 | 525430.4895 | 496077.5002 | 470107.845 | 450903.3411 | 435082.1713 | 419261.0014 | 403439.8315 | 387618.6617 | 371797.4918 | 355976.3219 | 340155.1521 | 324333.9822 | 308512.8123 | 292691.6425 | 276870.4726 | 261049.3028 | 245228.1329 | 229406.963 | 213585.7932 | 197764.6233 | 181943.4534 | 166122.2836 | 150301.1137 | 134479.9438 | 118658.774 | 102837.6041 | 87016.4343 | 71195.2644 | 55374.0945 | 39552.9247 | 23731.7548 | 7910.5849 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11 | 1.6371e-11
|  |  | Pre-Tax return on rate base | [5 empty] | 96512.1368 | 93613.8367 | 90319.1494 | 87165.5744 | 84142.5484 | 81240.3209 | 78449.8185 | 75762.6449 | 73133.1621 | 70511.9402 | 67890.7182 | 65269.4963 | 62648.2744 | 60027.0524 | 57405.8305 | 54784.6085 | 52163.3866 | 49542.1647 | 46920.9427 | 44299.7208 | 41980.6306 | 40265.6684 | 38852.8379 | 37440.0074 | 36027.177 | 34614.3465 | 33201.516 | 31788.6855 | 30375.8551 | 28963.0246 | 27550.1941 | 26137.3637 | 24724.5332 | 23311.7027 | 21898.8723 | 20486.0418 | 19073.2113 | 17660.3809 | 16247.5504 | 14834.7199 | 13421.8895 | 12009.059 | 10596.2285 | 9183.398 | 7770.5676 | 6357.7371 | 4944.9066 | 3532.0762 | 2119.2457 | 706.4152 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12 | 1.4619e-12
|  | Investment year in service | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95
|  | 2032 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
|  |  | Book depreciation | [6 empty] | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 22368.7288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service | [5 empty] | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 1118436.4391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation | [6 empty] | -22368.7288 | -44737.4576 | -67106.1863 | -89474.9151 | -111843.6439 | -134212.3727 | -156581.1015 | -178949.8303 | -201318.559 | -223687.2878 | -246056.0166 | -268424.7454 | -290793.4742 | -313162.203 | -335530.9317 | -357899.6605 | -380268.3893 | -402637.1181 | -425005.8469 | -447374.5757 | -469743.3044 | -492112.0332 | -514480.762 | -536849.4908 | -559218.2196 | -581586.9484 | -603955.6771 | -626324.4059 | -648693.1347 | -671061.8635 | -693430.5923 | -715799.3211 | -738168.0498 | -760536.7786 | -782905.5074 | -805274.2362 | -827642.965 | -850011.6938 | -872380.4225 | -894749.1513 | -917117.8801 | -939486.6089 | -961855.3377 | -984224.0664 | -1006592.7952 | -1028961.524 | -1051330.2528 | -1073698.9816 | -1096067.7104 | -1118436.4391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) | [6 empty] | 1118436.4391 | 1096067.7104 | 1073698.9816 | 1051330.2528 | 1028961.524 | 1006592.7952 | 984224.0664 | 961855.3377 | 939486.6089 | 917117.8801 | 894749.1513 | 872380.4225 | 850011.6938 | 827642.965 | 805274.2362 | 782905.5074 | 760536.7786 | 738168.0498 | 715799.3211 | 693430.5923 | 671061.8635 | 648693.1347 | 626324.4059 | 603955.6771 | 581586.9484 | 559218.2196 | 536849.4908 | 514480.762 | 492112.0332 | 469743.3044 | 447374.5757 | 425005.8469 | 402637.1181 | 380268.3893 | 357899.6605 | 335530.9317 | 313162.203 | 290793.4742 | 268424.7454 | 246056.0166 | 223687.2878 | 201318.559 | 178949.8303 | 156581.1015 | 134212.3727 | 111843.6439 | 89474.9151 | 67106.1863 | 44737.4576 | 22368.7288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) | [5 empty] | 1118436.4391 | 1096067.7104 | 1073698.9816 | 1051330.2528 | 1028961.524 | 1006592.7952 | 984224.0664 | 961855.3377 | 939486.6089 | 917117.8801 | 894749.1513 | 872380.4225 | 850011.6938 | 827642.965 | 805274.2362 | 782905.5074 | 760536.7786 | 738168.0498 | 715799.3211 | 693430.5923 | 671061.8635 | 648693.1347 | 626324.4059 | 603955.6771 | 581586.9484 | 559218.2196 | 536849.4908 | 514480.762 | 492112.0332 | 469743.3044 | 447374.5757 | 425005.8469 | 402637.1181 | 380268.3893 | 357899.6605 | 335530.9317 | 313162.203 | 290793.4742 | 268424.7454 | 246056.0166 | 223687.2878 | 201318.559 | 178949.8303 | 156581.1015 | 134212.3727 | 111843.6439 | 89474.9151 | 67106.1863 | 44737.4576 | 22368.7288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation | [6 empty] | 41941.3665 | 80739.9265 | 74678.001 | 69085.8188 | 63896.2738 | 59109.3658 | 54669.1731 | 50575.6958 | 49904.6339 | 49893.4496 | 49904.6339 | 49893.4496 | 49904.6339 | 49893.4496 | 49904.6339 | 49893.4496 | 49904.6339 | 49893.4496 | 49904.6339 | 49893.4496 | 24952.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) | [6 empty] | 0 | -5424.5565 | -21602.134 | -36099.6488 | -49047.2903 | -60556.6494 | -70739.317 | -79691.3851 | -87508.946 | -95140.5221 | -102768.9985 | -110400.5746 | -118029.0509 | -125660.6271 | -133289.1034 | -140920.6795 | -148549.1559 | -156180.732 | -163809.2084 | -171440.7845 | -179069.2608 | -179785.3023 | -173585.8091 | -167386.3159 | -161186.8227 | -154987.3296 | -148787.8364 | -142588.3432 | -136388.85 | -130189.3568 | -123989.8636 | -117790.3705 | -111590.8773 | -105391.3841 | -99191.8909 | -92992.3977 | -86792.9046 | -80593.4114 | -74393.9182 | -68194.425 | -61994.9318 | -55795.4386 | -49595.9455 | -43396.4523 | -37196.9591 | -30997.4659 | -24797.9727 | -18598.4795 | -12398.9864 | -6199.4932 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10
|  |  | ADIT (e.o.y.) | [6 empty] | -5424.5565 | -21602.134 | -36099.6488 | -49047.2903 | -60556.6494 | -70739.317 | -79691.3851 | -87508.946 | -95140.5221 | -102768.9985 | -110400.5746 | -118029.0509 | -125660.6271 | -133289.1034 | -140920.6795 | -148549.1559 | -156180.732 | -163809.2084 | -171440.7845 | -179069.2608 | -179785.3023 | -173585.8091 | -167386.3159 | -161186.8227 | -154987.3296 | -148787.8364 | -142588.3432 | -136388.85 | -130189.3568 | -123989.8636 | -117790.3705 | -111590.8773 | -105391.3841 | -99191.8909 | -92992.3977 | -86792.9046 | -80593.4114 | -74393.9182 | -68194.425 | -61994.9318 | -55795.4386 | -49595.9455 | -43396.4523 | -37196.9591 | -30997.4659 | -24797.9727 | -18598.4795 | -12398.9864 | -6199.4932 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10
|  |  | Net Rate Base | [6 empty] | 1104539.7965 | 1071370.0007 | 1033663.7258 | 997572.4188 | 962975.1898 | 929760.4477 | 897824.351 | 867070.8077 | 836977.5104 | 806978.7554 | 776980.0004 | 746981.2454 | 716982.4904 | 686983.7353 | 656984.9803 | 626986.2253 | 596987.4703 | 566988.7153 | 536989.9603 | 506991.2052 | 480450.2175 | 460823.2146 | 444653.979 | 428484.7434 | 412315.5078 | 396146.2722 | 379977.0366 | 363807.801 | 347638.5654 | 331469.3298 | 315300.0942 | 299130.8586 | 282961.623 | 266792.3874 | 250623.1518 | 234453.9162 | 218284.6806 | 202115.445 | 185946.2094 | 169776.9738 | 153607.7382 | 137438.5026 | 121269.267 | 105100.0314 | 88930.7958 | 72761.5602 | 56592.3246 | 40423.089 | 24253.8534 | 8084.6178 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10 | 1.4006e-10
|  |  | Pre-Tax return on rate base | [6 empty] | 98635.4038 | 95673.3411 | 92306.1707 | 89083.217 | 85993.6844 | 83027.608 | 80175.7145 | 77429.4231 | 74742.0917 | 72063.2029 | 69384.314 | 66705.4252 | 64026.5364 | 61347.6476 | 58668.7587 | 55989.8699 | 53310.9811 | 50632.0923 | 47953.2035 | 45274.3146 | 42904.2044 | 41151.5131 | 39707.6003 | 38263.6876 | 36819.7748 | 35375.8621 | 33931.9494 | 32488.0366 | 31044.1239 | 29600.2112 | 28156.2984 | 26712.3857 | 25268.4729 | 23824.5602 | 22380.6475 | 20936.7347 | 19492.822 | 18048.9092 | 16604.9965 | 15161.0838 | 13717.171 | 12273.2583 | 10829.3455 | 9385.4328 | 7941.5201 | 6497.6073 | 5053.6946 | 3609.7818 | 2165.8691 | 721.9564 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11 | 1.2508e-11
|  | Investment year in service | [7 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94
|  | 2033 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
|  |  | Book depreciation | [7 empty] | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 22860.8408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service | [6 empty] | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 1143042.0408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation | [7 empty] | -22860.8408 | -45721.6816 | -68582.5224 | -91443.3633 | -114304.2041 | -137165.0449 | -160025.8857 | -182886.7265 | -205747.5673 | -228608.4082 | -251469.249 | -274330.0898 | -297190.9306 | -320051.7714 | -342912.6122 | -365773.4531 | -388634.2939 | -411495.1347 | -434355.9755 | -457216.8163 | -480077.6571 | -502938.498 | -525799.3388 | -548660.1796 | -571521.0204 | -594381.8612 | -617242.702 | -640103.5429 | -662964.3837 | -685825.2245 | -708686.0653 | -731546.9061 | -754407.7469 | -777268.5877 | -800129.4286 | -822990.2694 | -845851.1102 | -868711.951 | -891572.7918 | -914433.6326 | -937294.4735 | -960155.3143 | -983016.1551 | -1005876.9959 | -1028737.8367 | -1051598.6775 | -1074459.5184 | -1097320.3592 | -1120181.2 | -1143042.0408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) | [7 empty] | 1143042.0408 | 1120181.2 | 1097320.3592 | 1074459.5184 | 1051598.6775 | 1028737.8367 | 1005876.9959 | 983016.1551 | 960155.3143 | 937294.4735 | 914433.6326 | 891572.7918 | 868711.951 | 845851.1102 | 822990.2694 | 800129.4286 | 777268.5877 | 754407.7469 | 731546.9061 | 708686.0653 | 685825.2245 | 662964.3837 | 640103.5429 | 617242.702 | 594381.8612 | 571521.0204 | 548660.1796 | 525799.3388 | 502938.498 | 480077.6571 | 457216.8163 | 434355.9755 | 411495.1347 | 388634.2939 | 365773.4531 | 342912.6122 | 320051.7714 | 297190.9306 | 274330.0898 | 251469.249 | 228608.4082 | 205747.5673 | 182886.7265 | 160025.8857 | 137165.0449 | 114304.2041 | 91443.3633 | 68582.5224 | 45721.6816 | 22860.8408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) | [6 empty] | 1143042.0408 | 1120181.2 | 1097320.3592 | 1074459.5184 | 1051598.6775 | 1028737.8367 | 1005876.9959 | 983016.1551 | 960155.3143 | 937294.4735 | 914433.6326 | 891572.7918 | 868711.951 | 845851.1102 | 822990.2694 | 800129.4286 | 777268.5877 | 754407.7469 | 731546.9061 | 708686.0653 | 685825.2245 | 662964.3837 | 640103.5429 | 617242.702 | 594381.8612 | 571521.0204 | 548660.1796 | 525799.3388 | 502938.498 | 480077.6571 | 457216.8163 | 434355.9755 | 411495.1347 | 388634.2939 | 365773.4531 | 342912.6122 | 320051.7714 | 297190.9306 | 274330.0898 | 251469.249 | 228608.4082 | 205747.5673 | 182886.7265 | 160025.8857 | 137165.0449 | 114304.2041 | 91443.3633 | 68582.5224 | 45721.6816 | 22860.8408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation | [7 empty] | 42864.0765 | 82516.2049 | 76320.9171 | 70605.7069 | 65301.9918 | 60409.7719 | 55871.895 | 51688.3611 | 51002.5359 | 50991.1054 | 51002.5359 | 50991.1054 | 51002.5359 | 50991.1054 | 51002.5359 | 50991.1054 | 51002.5359 | 50991.1054 | 51002.5359 | 50991.1054 | 25501.2679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) | [7 empty] | 0 | -5543.8968 | -22077.3809 | -36893.8411 | -50126.3307 | -61888.8957 | -72295.5819 | -81444.5956 | -89434.1428 | -97233.6136 | -105029.9164 | -112829.3872 | -120625.6901 | -128425.1609 | -136221.4637 | -144020.9345 | -151817.2373 | -159616.7081 | -167413.0109 | -175212.4817 | -183008.7846 | -183740.5789 | -177404.6969 | -171068.8149 | -164732.9328 | -158397.0508 | -152061.1688 | -145725.2867 | -139389.4047 | -133053.5227 | -126717.6406 | -120381.7586 | -114045.8766 | -107709.9945 | -101374.1125 | -95038.2305 | -88702.3485 | -82366.4664 | -76030.5844 | -69694.7024 | -63358.8203 | -57022.9383 | -50687.0563 | -44351.1742 | -38015.2922 | -31679.4102 | -25343.5281 | -19007.6461 | -12671.7641 | -6335.882 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11
|  |  | ADIT (e.o.y.) | [7 empty] | -5543.8968 | -22077.3809 | -36893.8411 | -50126.3307 | -61888.8957 | -72295.5819 | -81444.5956 | -89434.1428 | -97233.6136 | -105029.9164 | -112829.3872 | -120625.6901 | -128425.1609 | -136221.4637 | -144020.9345 | -151817.2373 | -159616.7081 | -167413.0109 | -175212.4817 | -183008.7846 | -183740.5789 | -177404.6969 | -171068.8149 | -164732.9328 | -158397.0508 | -152061.1688 | -145725.2867 | -139389.4047 | -133053.5227 | -126717.6406 | -120381.7586 | -114045.8766 | -107709.9945 | -101374.1125 | -95038.2305 | -88702.3485 | -82366.4664 | -76030.5844 | -69694.7024 | -63358.8203 | -57022.9383 | -50687.0563 | -44351.1742 | -38015.2922 | -31679.4102 | -25343.5281 | -19007.6461 | -12671.7641 | -6335.882 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11
|  |  | Net Rate Base | [7 empty] | 1128839.672 | 1094940.1407 | 1056404.3278 | 1019519.0121 | 984160.6439 | 950215.1775 | 917576.4867 | 886146.3655 | 855391.0157 | 824732.288 | 794073.5604 | 763414.8328 | 732756.1051 | 702097.3775 | 671438.6499 | 640779.9223 | 610121.1946 | 579462.467 | 548803.7394 | 518145.0118 | 491020.1223 | 470961.3253 | 454436.3666 | 437911.4078 | 421386.449 | 404861.4902 | 388336.5314 | 371811.5726 | 355286.6139 | 338761.6551 | 322236.6963 | 305711.7375 | 289186.7787 | 272661.8199 | 256136.8612 | 239611.9024 | 223086.9436 | 206561.9848 | 190037.026 | 173512.0672 | 156987.1084 | 140462.1497 | 123937.1909 | 107412.2321 | 90887.2733 | 74362.3145 | 57837.3557 | 41312.397 | 24787.4382 | 8262.4794 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11 | 5.8208e-11
|  |  | Pre-Tax return on rate base | [7 empty] | 100805.3827 | 97778.1546 | 94336.9065 | 91043.0478 | 87885.5455 | 84854.2154 | 81939.5803 | 79132.8704 | 76386.4177 | 73648.5933 | 70910.7689 | 68172.9446 | 65435.1202 | 62697.2958 | 59959.4714 | 57221.6471 | 54483.8227 | 51745.9983 | 49008.1739 | 46270.3495 | 43848.0969 | 42056.8464 | 40581.1675 | 39105.4887 | 37629.8099 | 36154.1311 | 34678.4523 | 33202.7734 | 31727.0946 | 30251.4158 | 28775.737 | 27300.0582 | 25824.3793 | 24348.7005 | 22873.0217 | 21397.3429 | 19921.6641 | 18445.9852 | 16970.3064 | 15494.6276 | 14018.9488 | 12543.27 | 11067.5911 | 9591.9123 | 8116.2335 | 6640.5547 | 5164.8759 | 3689.197 | 2213.5182 | 737.8394 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12 | 5.1979e-12
|  | Investment year in service | [8 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93
|  | 2034 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
|  |  | Book depreciation | [8 empty] | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 23363.7793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service | [7 empty] | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 1168188.9657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation | [8 empty] | -23363.7793 | -46727.5586 | -70091.3379 | -93455.1173 | -116818.8966 | -140182.6759 | -163546.4552 | -186910.2345 | -210274.0138 | -233637.7931 | -257001.5725 | -280365.3518 | -303729.1311 | -327092.9104 | -350456.6897 | -373820.469 | -397184.2483 | -420548.0277 | -443911.807 | -467275.5863 | -490639.3656 | -514003.1449 | -537366.9242 | -560730.7035 | -584094.4829 | -607458.2622 | -630822.0415 | -654185.8208 | -677549.6001 | -700913.3794 | -724277.1587 | -747640.9381 | -771004.7174 | -794368.4967 | -817732.276 | -841096.0553 | -864459.8346 | -887823.6139 | -911187.3932 | -934551.1726 | -957914.9519 | -981278.7312 | -1004642.5105 | -1028006.2898 | -1051370.0691 | -1074733.8484 | -1098097.6278 | -1121461.4071 | -1144825.1864 | -1168188.9657 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) | [8 empty] | 1168188.9657 | 1144825.1864 | 1121461.4071 | 1098097.6278 | 1074733.8484 | 1051370.0691 | 1028006.2898 | 1004642.5105 | 981278.7312 | 957914.9519 | 934551.1726 | 911187.3932 | 887823.6139 | 864459.8346 | 841096.0553 | 817732.276 | 794368.4967 | 771004.7174 | 747640.9381 | 724277.1587 | 700913.3794 | 677549.6001 | 654185.8208 | 630822.0415 | 607458.2622 | 584094.4829 | 560730.7035 | 537366.9242 | 514003.1449 | 490639.3656 | 467275.5863 | 443911.807 | 420548.0277 | 397184.2483 | 373820.469 | 350456.6897 | 327092.9104 | 303729.1311 | 280365.3518 | 257001.5725 | 233637.7931 | 210274.0138 | 186910.2345 | 163546.4552 | 140182.6759 | 116818.8966 | 93455.1173 | 70091.3379 | 46727.5586 | 23363.7793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) | [7 empty] | 1168188.9657 | 1144825.1864 | 1121461.4071 | 1098097.6278 | 1074733.8484 | 1051370.0691 | 1028006.2898 | 1004642.5105 | 981278.7312 | 957914.9519 | 934551.1726 | 911187.3932 | 887823.6139 | 864459.8346 | 841096.0553 | 817732.276 | 794368.4967 | 771004.7174 | 747640.9381 | 724277.1587 | 700913.3794 | 677549.6001 | 654185.8208 | 630822.0415 | 607458.2622 | 584094.4829 | 560730.7035 | 537366.9242 | 514003.1449 | 490639.3656 | 467275.5863 | 443911.807 | 420548.0277 | 397184.2483 | 373820.469 | 350456.6897 | 327092.9104 | 303729.1311 | 280365.3518 | 257001.5725 | 233637.7931 | 210274.0138 | 186910.2345 | 163546.4552 | 140182.6759 | 116818.8966 | 93455.1173 | 70091.3379 | 46727.5586 | 23363.7793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation | [8 empty] | 43807.0862 | 84331.5614 | 77999.9772 | 72159.0324 | 66738.6356 | 61738.7868 | 57101.0766 | 52825.505 | 52124.5916 | 52112.9098 | 52124.5916 | 52112.9098 | 52124.5916 | 52112.9098 | 52124.5916 | 52112.9098 | 52124.5916 | 52112.9098 | 52124.5916 | 52112.9098 | 26062.2958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) | [8 empty] | 0 | -5665.8625 | -22563.0833 | -37705.5056 | -51229.11 | -63250.4514 | -73886.0847 | -83236.3767 | -91401.694 | -99372.7531 | -107340.5746 | -115311.6337 | -123279.4553 | -131250.5144 | -139218.3359 | -147189.395 | -155157.2165 | -163128.2757 | -171096.0972 | -179067.1563 | -187034.9778 | -187782.8717 | -181307.6002 | -174832.3288 | -168357.0574 | -161881.7859 | -155406.5145 | -148931.243 | -142455.9716 | -135980.7002 | -129505.4287 | -123030.1573 | -116554.8859 | -110079.6144 | -103604.343 | -97129.0716 | -90653.8001 | -84178.5287 | -77703.2572 | -71227.9858 | -64752.7144 | -58277.4429 | -51802.1715 | -45326.9001 | -38851.6286 | -32376.3572 | -25901.0857 | -19425.8143 | -12950.5429 | -6475.2714 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11
|  |  | ADIT (e.o.y.) | [8 empty] | -5665.8625 | -22563.0833 | -37705.5056 | -51229.11 | -63250.4514 | -73886.0847 | -83236.3767 | -91401.694 | -99372.7531 | -107340.5746 | -115311.6337 | -123279.4553 | -131250.5144 | -139218.3359 | -147189.395 | -155157.2165 | -163128.2757 | -171096.0972 | -179067.1563 | -187034.9778 | -187782.8717 | -181307.6002 | -174832.3288 | -168357.0574 | -161881.7859 | -155406.5145 | -148931.243 | -142455.9716 | -135980.7002 | -129505.4287 | -123030.1573 | -116554.8859 | -110079.6144 | -103604.343 | -97129.0716 | -90653.8001 | -84178.5287 | -77703.2572 | -71227.9858 | -64752.7144 | -58277.4429 | -51802.1715 | -45326.9001 | -38851.6286 | -32376.3572 | -25901.0857 | -19425.8143 | -12950.5429 | -6475.2714 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11
|  |  | Net Rate Base | [8 empty] | 1153674.1448 | 1119028.8238 | 1079645.223 | 1041948.4303 | 1005812.1781 | 971119.9114 | 937763.1695 | 905641.5855 | 874209.618 | 842876.3984 | 811543.1787 | 780209.9591 | 748876.7395 | 717543.5198 | 686210.3002 | 654877.0806 | 623543.8609 | 592210.6413 | 560877.4216 | 529544.202 | 501822.565 | 481322.4745 | 464433.9666 | 447545.4587 | 430656.9509 | 413768.443 | 396879.9351 | 379991.4272 | 363102.9194 | 346214.4115 | 329325.9036 | 312437.3957 | 295548.8879 | 278660.38 | 261771.8721 | 244883.3642 | 227994.8563 | 211106.3485 | 194217.8406 | 177329.3327 | 160440.8248 | 143552.317 | 126663.8091 | 109775.3012 | 92886.7933 | 75998.2854 | 59109.7776 | 42221.2697 | 25332.7618 | 8444.2539 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11 | -5.8208e-11
|  |  | Pre-Tax return on rate base | [8 empty] | 103023.1011 | 99929.274 | 96412.3184 | 93045.9948 | 89819.0275 | 86721.0081 | 83742.251 | 80873.7936 | 78066.9189 | 75268.8624 | 72470.8059 | 69672.7493 | 66874.6928 | 64076.6363 | 61278.5798 | 58480.5233 | 55682.4668 | 52884.4103 | 50086.3538 | 47288.2972 | 44812.7551 | 42982.097 | 41473.9532 | 39965.8095 | 38457.6657 | 36949.522 | 35441.3782 | 33933.2345 | 32425.0907 | 30916.9469 | 29408.8032 | 27900.6594 | 26392.5157 | 24884.3719 | 23376.2282 | 21868.0844 | 20359.9407 | 18851.7969 | 17343.6532 | 15835.5094 | 14327.3657 | 12819.2219 | 11311.0782 | 9802.9344 | 8294.7906 | 6786.6469 | 5278.5031 | 3770.3594 | 2262.2156 | 754.0719 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12 | -5.1979e-12
|  | Investment year in service | [9 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92
|  | 2035 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
|  |  | Book depreciation | [9 empty] | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 23877.7825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service | [8 empty] | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 1193889.1229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation | [9 empty] | -23877.7825 | -47755.5649 | -71633.3474 | -95511.1298 | -119388.9123 | -143266.6948 | -167144.4772 | -191022.2597 | -214900.0421 | -238777.8246 | -262655.607 | -286533.3895 | -310411.172 | -334288.9544 | -358166.7369 | -382044.5193 | -405922.3018 | -429800.0843 | -453677.8667 | -477555.6492 | -501433.4316 | -525311.2141 | -549188.9966 | -573066.779 | -596944.5615 | -620822.3439 | -644700.1264 | -668577.9089 | -692455.6913 | -716333.4738 | -740211.2562 | -764089.0387 | -787966.8211 | -811844.6036 | -835722.3861 | -859600.1685 | -883477.951 | -907355.7334 | -931233.5159 | -955111.2984 | -978989.0808 | -1002866.8633 | -1026744.6457 | -1050622.4282 | -1074500.2107 | -1098377.9931 | -1122255.7756 | -1146133.558 | -1170011.3405 | -1193889.1229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) | [9 empty] | 1193889.1229 | 1170011.3405 | 1146133.558 | 1122255.7756 | 1098377.9931 | 1074500.2107 | 1050622.4282 | 1026744.6457 | 1002866.8633 | 978989.0808 | 955111.2984 | 931233.5159 | 907355.7334 | 883477.951 | 859600.1685 | 835722.3861 | 811844.6036 | 787966.8211 | 764089.0387 | 740211.2562 | 716333.4738 | 692455.6913 | 668577.9089 | 644700.1264 | 620822.3439 | 596944.5615 | 573066.779 | 549188.9966 | 525311.2141 | 501433.4316 | 477555.6492 | 453677.8667 | 429800.0843 | 405922.3018 | 382044.5193 | 358166.7369 | 334288.9544 | 310411.172 | 286533.3895 | 262655.607 | 238777.8246 | 214900.0421 | 191022.2597 | 167144.4772 | 143266.6948 | 119388.9123 | 95511.1298 | 71633.3474 | 47755.5649 | 23877.7825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) | [8 empty] | 1193889.1229 | 1170011.3405 | 1146133.558 | 1122255.7756 | 1098377.9931 | 1074500.2107 | 1050622.4282 | 1026744.6457 | 1002866.8633 | 978989.0808 | 955111.2984 | 931233.5159 | 907355.7334 | 883477.951 | 859600.1685 | 835722.3861 | 811844.6036 | 787966.8211 | 764089.0387 | 740211.2562 | 716333.4738 | 692455.6913 | 668577.9089 | 644700.1264 | 620822.3439 | 596944.5615 | 573066.779 | 549188.9966 | 525311.2141 | 501433.4316 | 477555.6492 | 453677.8667 | 429800.0843 | 405922.3018 | 382044.5193 | 358166.7369 | 334288.9544 | 310411.172 | 286533.3895 | 262655.607 | 238777.8246 | 214900.0421 | 191022.2597 | 167144.4772 | 143266.6948 | 119388.9123 | 95511.1298 | 71633.3474 | 47755.5649 | 23877.7825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation | [9 empty] | 44770.8421 | 86186.8558 | 79715.9767 | 73746.5311 | 68206.8856 | 63097.0401 | 58357.3003 | 53987.6661 | 53271.3327 | 53259.3938 | 53271.3327 | 53259.3938 | 53271.3327 | 53259.3938 | 53271.3327 | 53259.3938 | 53271.3327 | 53259.3938 | 53271.3327 | 53259.3938 | 26635.6663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) | [9 empty] | 0 | -5790.5115 | -23059.4712 | -38535.0267 | -52356.1504 | -64641.9613 | -75511.5786 | -85067.577 | -93412.5312 | -101558.9537 | -109702.0673 | -117848.4897 | -125991.6033 | -134138.0257 | -142281.1393 | -150427.5617 | -158570.6753 | -166717.0977 | -174860.2113 | -183006.6338 | -191149.7473 | -191914.0948 | -185296.3674 | -178678.64 | -172060.9126 | -165443.1852 | -158825.4578 | -152207.7304 | -145590.003 | -138972.2756 | -132354.5482 | -125736.8208 | -119119.0934 | -112501.3659 | -105883.6385 | -99265.9111 | -92648.1837 | -86030.4563 | -79412.7289 | -72795.0015 | -66177.2741 | -59559.5467 | -52941.8193 | -46324.0919 | -39706.3645 | -33088.637 | -26470.9096 | -19853.1822 | -13235.4548 | -6617.7274 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11
|  |  | ADIT (e.o.y.) | [9 empty] | -5790.5115 | -23059.4712 | -38535.0267 | -52356.1504 | -64641.9613 | -75511.5786 | -85067.577 | -93412.5312 | -101558.9537 | -109702.0673 | -117848.4897 | -125991.6033 | -134138.0257 | -142281.1393 | -150427.5617 | -158570.6753 | -166717.0977 | -174860.2113 | -183006.6338 | -191149.7473 | -191914.0948 | -185296.3674 | -178678.64 | -172060.9126 | -165443.1852 | -158825.4578 | -152207.7304 | -145590.003 | -138972.2756 | -132354.5482 | -125736.8208 | -119119.0934 | -112501.3659 | -105883.6385 | -99265.9111 | -92648.1837 | -86030.4563 | -79412.7289 | -72795.0015 | -66177.2741 | -59559.5467 | -52941.8193 | -46324.0919 | -39706.3645 | -33088.637 | -26470.9096 | -19853.1822 | -13235.4548 | -6617.7274 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11
|  |  | Net Rate Base | [9 empty] | 1179054.976 | 1143647.4579 | 1103397.4179 | 1064871.2958 | 1027940.046 | 992484.5495 | 958393.9592 | 925565.7004 | 893442.2296 | 861419.6791 | 829397.1287 | 797374.5782 | 765352.0277 | 733329.4773 | 701306.9268 | 669284.3763 | 637261.8259 | 605239.2754 | 573216.7249 | 541194.1745 | 512862.6615 | 491911.5689 | 474651.5139 | 457391.4588 | 440131.4038 | 422871.3487 | 405611.2937 | 388351.2386 | 371091.1836 | 353831.1285 | 336571.0735 | 319311.0184 | 302050.9634 | 284790.9083 | 267530.8533 | 250270.7982 | 233010.7432 | 215750.6881 | 198490.6331 | 181230.578 | 163970.523 | 146710.4679 | 129450.4129 | 112190.3578 | 94930.3028 | 77670.2477 | 60410.1927 | 43150.1376 | 25890.0826 | 8630.0275 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11 | 5.2751e-11
|  |  | Pre-Tax return on rate base | [9 empty] | 105289.6094 | 102127.718 | 98533.3894 | 95093.0067 | 91795.0461 | 88628.8703 | 85584.5806 | 82653.017 | 79784.3911 | 76924.7773 | 74065.1636 | 71205.5498 | 68345.9361 | 65486.3223 | 62626.7086 | 59767.0948 | 56907.481 | 54047.8673 | 51188.2535 | 48328.6398 | 45798.6357 | 43927.7031 | 42386.3802 | 40845.0573 | 39303.7344 | 37762.4114 | 36221.0885 | 34679.7656 | 33138.4427 | 31597.1198 | 30055.7969 | 28514.4739 | 26973.151 | 25431.8281 | 23890.5052 | 22349.1823 | 20807.8594 | 19266.5365 | 17725.2135 | 16183.8906 | 14642.5677 | 13101.2448 | 11559.9219 | 10018.599 | 8477.276 | 6935.9531 | 5394.6302 | 3853.3073 | 2311.9844 | 770.6615 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12 | 4.7106e-12
|  | Investment year in service | [10 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91
|  | 2036 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
|  |  | Book depreciation | [10 empty] | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 24403.0937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service | [9 empty] | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 1220154.6837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation | [10 empty] | -24403.0937 | -48806.1873 | -73209.281 | -97612.3747 | -122015.4684 | -146418.562 | -170821.6557 | -195224.7494 | -219627.8431 | -244030.9367 | -268434.0304 | -292837.1241 | -317240.2178 | -341643.3114 | -366046.4051 | -390449.4988 | -414852.5924 | -439255.6861 | -463658.7798 | -488061.8735 | -512464.9671 | -536868.0608 | -561271.1545 | -585674.2482 | -610077.3418 | -634480.4355 | -658883.5292 | -683286.6228 | -707689.7165 | -732092.8102 | -756495.9039 | -780898.9975 | -805302.0912 | -829705.1849 | -854108.2786 | -878511.3722 | -902914.4659 | -927317.5596 | -951720.6533 | -976123.7469 | -1000526.8406 | -1024929.9343 | -1049333.0279 | -1073736.1216 | -1098139.2153 | -1122542.309 | -1146945.4026 | -1171348.4963 | -1195751.59 | -1220154.6837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) | [10 empty] | 1220154.6837 | 1195751.59 | 1171348.4963 | 1146945.4026 | 1122542.309 | 1098139.2153 | 1073736.1216 | 1049333.0279 | 1024929.9343 | 1000526.8406 | 976123.7469 | 951720.6533 | 927317.5596 | 902914.4659 | 878511.3722 | 854108.2786 | 829705.1849 | 805302.0912 | 780898.9975 | 756495.9039 | 732092.8102 | 707689.7165 | 683286.6228 | 658883.5292 | 634480.4355 | 610077.3418 | 585674.2482 | 561271.1545 | 536868.0608 | 512464.9671 | 488061.8735 | 463658.7798 | 439255.6861 | 414852.5924 | 390449.4988 | 366046.4051 | 341643.3114 | 317240.2178 | 292837.1241 | 268434.0304 | 244030.9367 | 219627.8431 | 195224.7494 | 170821.6557 | 146418.562 | 122015.4684 | 97612.3747 | 73209.281 | 48806.1873 | 24403.0937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) | [9 empty] | 1220154.6837 | 1195751.59 | 1171348.4963 | 1146945.4026 | 1122542.309 | 1098139.2153 | 1073736.1216 | 1049333.0279 | 1024929.9343 | 1000526.8406 | 976123.7469 | 951720.6533 | 927317.5596 | 902914.4659 | 878511.3722 | 854108.2786 | 829705.1849 | 805302.0912 | 780898.9975 | 756495.9039 | 732092.8102 | 707689.7165 | 683286.6228 | 658883.5292 | 634480.4355 | 610077.3418 | 585674.2482 | 561271.1545 | 536868.0608 | 512464.9671 | 488061.8735 | 463658.7798 | 439255.6861 | 414852.5924 | 390449.4988 | 366046.4051 | 341643.3114 | 317240.2178 | 292837.1241 | 268434.0304 | 244030.9367 | 219627.8431 | 195224.7494 | 170821.6557 | 146418.562 | 122015.4684 | 97612.3747 | 73209.281 | 48806.1873 | 24403.0937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation | [10 empty] | 45755.8006 | 88082.9666 | 81469.7282 | 75368.9548 | 69707.4371 | 64485.175 | 59641.1609 | 55175.3948 | 54443.302 | 54431.1004 | 54443.302 | 54431.1004 | 54443.302 | 54431.1004 | 54443.302 | 54431.1004 | 54443.302 | 54431.1004 | 54443.302 | 54431.1004 | 27221.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) | [10 empty] | 0 | -5917.9027 | -23566.7795 | -39382.7973 | -53507.9857 | -66064.0845 | -77172.8333 | -86939.0637 | -95467.6069 | -103793.2507 | -112115.5127 | -120441.1565 | -128763.4185 | -137089.0623 | -145411.3243 | -153736.9681 | -162059.2302 | -170384.8739 | -178707.136 | -187032.7797 | -195355.0418 | -196136.2049 | -189372.8875 | -182609.5701 | -175846.2527 | -169082.9353 | -162319.6179 | -155556.3005 | -148792.9831 | -142029.6656 | -135266.3482 | -128503.0308 | -121739.7134 | -114976.396 | -108213.0786 | -101449.7612 | -94686.4438 | -87923.1263 | -81159.8089 | -74396.4915 | -67633.1741 | -60869.8567 | -54106.5393 | -47343.2219 | -40579.9045 | -33816.5871 | -27053.2696 | -20289.9522 | -13526.6348 | -6763.3174 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10
|  |  | ADIT (e.o.y.) | [10 empty] | -5917.9027 | -23566.7795 | -39382.7973 | -53507.9857 | -66064.0845 | -77172.8333 | -86939.0637 | -95467.6069 | -103793.2507 | -112115.5127 | -120441.1565 | -128763.4185 | -137089.0623 | -145411.3243 | -153736.9681 | -162059.2302 | -170384.8739 | -178707.136 | -187032.7797 | -195355.0418 | -196136.2049 | -189372.8875 | -182609.5701 | -175846.2527 | -169082.9353 | -162319.6179 | -155556.3005 | -148792.9831 | -142029.6656 | -135266.3482 | -128503.0308 | -121739.7134 | -114976.396 | -108213.0786 | -101449.7612 | -94686.4438 | -87923.1263 | -81159.8089 | -74396.4915 | -67633.1741 | -60869.8567 | -54106.5393 | -47343.2219 | -40579.9045 | -33816.5871 | -27053.2696 | -20289.9522 | -13526.6348 | -6763.3174 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10
|  |  | Net Rate Base | [10 empty] | 1204994.1855 | 1168807.702 | 1127672.1611 | 1088298.4643 | 1050554.727 | 1014319.2096 | 979478.6263 | 945928.1458 | 913097.9586 | 880370.9121 | 847643.8655 | 814916.8189 | 782189.7723 | 749462.7258 | 716735.6792 | 684008.6326 | 651281.586 | 618554.5394 | 585827.4929 | 553100.4463 | 524145.64 | 502733.6235 | 485093.8472 | 467454.0709 | 449814.2947 | 432174.5184 | 414534.7421 | 396894.9659 | 379255.1896 | 361615.4134 | 343975.6371 | 326335.8608 | 308696.0846 | 291056.3083 | 273416.5321 | 255776.7558 | 238136.9795 | 220497.2033 | 202857.427 | 185217.6507 | 167577.8745 | 149938.0982 | 132298.322 | 114658.5457 | 97018.7694 | 79378.9932 | 61739.2169 | 44099.4407 | 26459.6644 | 8819.8881 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10 | 1.0368e-10
|  |  | Pre-Tax return on rate base | [10 empty] | 107605.9808 | 104374.5278 | 100701.124 | 97185.0529 | 93814.5371 | 90578.7054 | 87467.4413 | 84471.3834 | 81539.6477 | 78617.1224 | 75694.5972 | 72772.0719 | 69849.5467 | 66927.0214 | 64004.4962 | 61081.9709 | 58159.4456 | 55236.9204 | 52314.3951 | 49391.8699 | 46806.2057 | 44894.1126 | 43318.8806 | 41743.6485 | 40168.4165 | 38593.1845 | 37017.9525 | 35442.7205 | 33867.4884 | 32292.2564 | 30717.0244 | 29141.7924 | 27566.5604 | 25991.3283 | 24416.0963 | 22840.8643 | 21265.6323 | 19690.4003 | 18115.1682 | 16539.9362 | 14964.7042 | 13389.4722 | 11814.2402 | 10239.0081 | 8663.7761 | 7088.5441 | 5513.3121 | 3938.0801 | 2362.848 | 787.616 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12 | 9.2588e-12
|  |  | Total CAPEX cost rollup |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100
|  |  | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
|  |  | Book depreciation | 0 | 20062.582 | 40566.5408 | 61521.5867 | 82937.6436 | 104824.8538 | 127193.5826 | 150054.4234 | 173418.2027 | 197295.9851 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 221699.0788 | 201636.4968 | 181132.538 | 160177.4921 | 138761.4352 | 116874.225 | 94505.4963 | 71644.6554 | 48280.8761 | 24403.0937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service | 1003129.1 | 1003129.1 | 2028327.0402 | 3076079.3351 | 4146882.1805 | 5241242.6884 | 6359679.1276 | 7502721.1684 | 8670910.1341 | 8670910.1341 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 11084953.9407 | 10081824.8407 | 9056626.9005 | 8008874.6056 | 6938071.7602 | 5843711.2523 | 4725274.8131 | 3582232.7723 | 2414043.8066 | 1220154.6837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation | 0 | -20062.582 | -60629.1228 | -122150.7095 | -205088.3531 | -309913.2069 | -437106.7894 | -587161.2128 | -760579.4155 | -957875.4006 | -1179574.4794 | -1401273.5583 | -1622972.6371 | -1844671.7159 | -2066370.7947 | -2288069.8735 | -2509768.9523 | -2731468.0311 | -2953167.1099 | -3174866.1888 | -3396565.2676 | -3618264.3464 | -3839963.4252 | -4061662.504 | -4283361.5828 | -4505060.6616 | -4726759.7405 | -4948458.8193 | -5170157.8981 | -5391856.9769 | -5613556.0557 | -5835255.1345 | -6056954.2133 | -6278653.2922 | -6500352.371 | -6722051.4498 | -6943750.5286 | -7165449.6074 | -7387148.6862 | -7608847.765 | -7830546.8439 | -8052245.9227 | -8273945.0015 | -8495644.0803 | -8717343.1591 | -8939042.2379 | -9160741.3167 | -9382440.3955 | -9604139.4744 | -9825838.5532 | -10047537.632 | -9246045.0288 | -8401979.6266 | -7514404.8238 | -6582363.4137 | -5604877.1307 | -4580946.1879 | -3509548.8025 | -2389640.7129 | -1220154.6837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) | 0 | 1003129.1 | 2008264.4582 | 3015450.2123 | 4024731.471 | 5036154.3353 | 6049765.9207 | 7065614.3789 | 8083748.9213 | 9104219.8415 | 10127078.5401 | 9905379.4612 | 9683680.3824 | 9461981.3036 | 9240282.2248 | 9018583.146 | 8796884.0672 | 8575184.9884 | 8353485.9096 | 8131786.8307 | 7910087.7519 | 7688388.6731 | 7466689.5943 | 7244990.5155 | 7023291.4367 | 6801592.3579 | 6579893.279 | 6358194.2002 | 6136495.1214 | 5914796.0426 | 5693096.9638 | 5471397.885 | 5249698.8062 | 5027999.7273 | 4806300.6485 | 4584601.5697 | 4362902.4909 | 4141203.4121 | 3919504.3333 | 3697805.2545 | 3476106.1757 | 3254407.0968 | 3032708.018 | 2811008.9392 | 2589309.8604 | 2367610.7816 | 2145911.7028 | 1924212.624 | 1702513.5451 | 1480814.4663 | 1259115.3875 | 1037416.3087 | 835779.8119 | 654647.2739 | 494469.7818 | 355708.3466 | 238834.1215 | 144328.6253 | 72683.9698 | 24403.0937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) | 1003129.1 | 2008264.4582 | 3015450.2123 | 4024731.471 | 5036154.3353 | 6049765.9207 | 7065614.3789 | 8083748.9213 | 9104219.8415 | 10127078.5401 | 9905379.4612 | 9683680.3824 | 9461981.3036 | 9240282.2248 | 9018583.146 | 8796884.0672 | 8575184.9884 | 8353485.9096 | 8131786.8307 | 7910087.7519 | 7688388.6731 | 7466689.5943 | 7244990.5155 | 7023291.4367 | 6801592.3579 | 6579893.279 | 6358194.2002 | 6136495.1214 | 5914796.0426 | 5693096.9638 | 5471397.885 | 5249698.8062 | 5027999.7273 | 4806300.6485 | 4584601.5697 | 4362902.4909 | 4141203.4121 | 3919504.3333 | 3697805.2545 | 3476106.1757 | 3254407.0968 | 3032708.018 | 2811008.9392 | 2589309.8604 | 2367610.7816 | 2145911.7028 | 1924212.624 | 1702513.5451 | 1480814.4663 | 1259115.3875 | 1037416.3087 | 835779.8119 | 654647.2739 | 494469.7818 | 355708.3466 | 238834.1215 | 144328.6253 | 72683.9698 | 24403.0937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation | 0 | 37617.3413 | 110860.8125 | 180278.6804 | 246208.0958 | 308933.4394 | 368745.348 | 425890.6961 | 480621.7893 | 535955.0891 | 592495.6902 | 603527.7876 | 571534.1962 | 545605.5067 | 525331.3452 | 510407.2546 | 500481.9544 | 495298.9114 | 494555.8231 | 494554.617 | 494555.8231 | 472174.8068 | 426934.0679 | 380685.5628 | 333432.0605 | 285126.5112 | 235770.7098 | 185316.6108 | 133764.9916 | 81066.7668 | 27221.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) | 0 | 0 | -4865.3015 | -24347.3589 | -57260.8874 | -102511.2933 | -159079.9878 | -226026.0596 | -302474.0826 | -387615.5566 | -481474.9273 | -584241.2081 | -690065.0348 | -787021.8376 | -876792.5041 | -960944.1867 | -1040959.6576 | -1118224.3316 | -1194052.5252 | -1269674.7719 | -1345296.6843 | -1420918.9309 | -1490338.279 | -1547219.1562 | -1591282.2602 | -1622249.0561 | -1639827.969 | -1643727.9215 | -1633644.5205 | -1609273.5882 | -1570297.3429 | -1516397.9238 | -1454954.0241 | -1393510.1244 | -1332066.2247 | -1270622.325 | -1209178.4254 | -1147734.5257 | -1086290.626 | -1024846.7263 | -963402.8266 | -901958.9269 | -840515.0272 | -779071.1275 | -717627.2278 | -656183.3281 | -594739.4284 | -533295.5287 | -471851.629 | -410407.7293 | -348963.8296 | -287519.93 | -231636.3749 | -181435.492 | -137042.3 | -98584.5682 | -66192.8768 | -40000.6785 | -20144.3622 | -6763.3174 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10
|  |  | ADIT (e.o.y.) | 0 | -4865.3015 | -24347.3589 | -57260.8874 | -102511.2933 | -159079.9878 | -226026.0596 | -302474.0826 | -387615.5566 | -481474.9273 | -584241.2081 | -690065.0348 | -787021.8376 | -876792.5041 | -960944.1867 | -1040959.6576 | -1118224.3316 | -1194052.5252 | -1269674.7719 | -1345296.6843 | -1420918.9309 | -1490338.279 | -1547219.1562 | -1591282.2602 | -1622249.0561 | -1639827.969 | -1643727.9215 | -1633644.5205 | -1609273.5882 | -1570297.3429 | -1516397.9238 | -1454954.0241 | -1393510.1244 | -1332066.2247 | -1270622.325 | -1209178.4254 | -1147734.5257 | -1086290.626 | -1024846.7263 | -963402.8266 | -901958.9269 | -840515.0272 | -779071.1275 | -717627.2278 | -656183.3281 | -594739.4284 | -533295.5287 | -471851.629 | -410407.7293 | -348963.8296 | -287519.93 | -231636.3749 | -181435.492 | -137042.3 | -98584.5682 | -66192.8768 | -40000.6785 | -20144.3622 | -6763.3174 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10
|  |  | Net Rate Base | 0 | 990665.1582 | 1973374.8576 | 2943885.2958 | 3903376.5588 | 4852946.2679 | 5793616.1057 | 6726337.0962 | 7651995.0003 | 8571026.607 | 9483370.9329 | 9157376.8004 | 8834287.4068 | 8519224.5934 | 8210564.34 | 7906781.6844 | 7606442.5332 | 7308197.0206 | 7010772.7216 | 6713451.5633 | 6416130.4049 | 6121910.5287 | 5837061.3373 | 5564890.2679 | 5305676.2391 | 5059704.3059 | 4827265.7944 | 4608658.4398 | 4404186.5276 | 4214161.0376 | 4038899.791 | 3874872.3716 | 3714617.1925 | 3554362.0134 | 3394106.8342 | 3233851.6551 | 3073596.476 | 2913341.2969 | 2753086.1177 | 2592830.9386 | 2432575.7595 | 2272320.5804 | 2112065.4013 | 1951810.2221 | 1791555.043 | 1631299.8639 | 1471044.6848 | 1310789.5057 | 1150534.3265 | 990279.1474 | 830023.9683 | 677019.9079 | 538677.6095 | 415319.6318 | 307275.63 | 214882.5115 | 138484.5957 | 78433.7772 | 35089.6919 | 8819.8881 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10 | 3.9654e-10
|  |  | Pre-Tax return on rate base | 0 | 88466.3986 | 176222.3748 | 262888.9569 | 348571.5267 | 433368.1017 | 517369.9182 | 600661.9027 | 683323.1535 | 765392.676 | 846865.0243 | 817753.7483 | 788901.8654 | 760766.7562 | 733203.3956 | 706075.6044 | 679255.3182 | 652621.9939 | 626062.004 | 599511.2246 | 572960.4452 | 546686.6102 | 521249.5774 | 496944.7009 | 473796.8882 | 451831.5945 | 431074.8354 | 411553.1987 | 393293.8569 | 376324.5807 | 360673.7513 | 346026.1028 | 331715.3153 | 317404.5278 | 303093.7403 | 288782.9528 | 274472.1653 | 260161.3778 | 245850.5903 | 231539.8028 | 217229.0153 | 202918.2278 | 188607.4403 | 174296.6528 | 159985.8653 | 145675.0778 | 131364.2904 | 117053.5029 | 102742.7154 | 88431.9279 | 74121.1404 | 60457.8778 | 48103.9105 | 37088.0431 | 27439.7138 | 19189.0083 | 12366.6744 | 7004.1363 | 3133.5095 | 787.616 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11 | 3.5411e-11

## Rev Req't_Baseline_OH3PH
Assumptions | Value
Equipment Life flag | 47 |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100
Book life flag | 50 |  |  | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
MACRS flag | 20 |  | Unescalated Baseline Costs (from Construction, with Overheads) | 1 2028: 3612272.3; 2 2029: 3612272.3; 3 2030: 3612272.3; 4 2031: 3612272.3; 5 2032: 3612272.3; 6 2033: 3612272.3; 7 2034: 3612272.3; 8 2035: 3612272.3; 9 2036: 3612272.3; 10 2037: 3612272.3
|  |  | Miles unescalated | 1 2028: 5.132; 2 2029: 5.132; 3 2030: 5.132; 4 2031: 5.132; 5 2032: 5.132; 6 2033: 5.132; 7 2034: 5.132; 8 2035: 5.132; 9 2036: 5.132; 10 2037: 5.132
|  |  | Cost per mile unescalated | 1 2028: 703872.233; 2 2029: 703872.233; 3 2030: 703872.233; 4 2031: 703872.233; 5 2032: 703872.233; 6 2033: 703872.233; 7 2034: 703872.233; 8 2035: 703872.233; 9 2036: 703872.233; 10 2037: 703872.233
|  |  | CPI | 1 2028: 1; 2 2029: 1.022; 3 2030: 1.0445; 4 2031: 1.0675; 5 2032: 1.0909; 6 2033: 1.1149; 7 2034: 1.1395; 8 2035: 1.1645; 9 2036: 1.1902; 10 2037: 1.2163
|  |  | Escalated with CPI | 1 2028: 3612272.3; 2 2029: 3691742.2906; 3 2030: 3772960.621; 4 2031: 3855965.7547; 5 2032: 3940797.0013; 6 2033: 4027494.5353; 7 2034: 4116099.4151; 8 2035: 4206653.6022; 9 2036: 4299199.9814; 10 2037: 4393782.381
|  |  | Cost per mile escalated | 1 2028: 703872.233; 2 2029: 719357.4222; 3 2030: 735183.2855; 4 2031: 751357.3177; 5 2032: 767887.1787; 6 2033: 784780.6967; 7 2034: 802045.872; 8 2035: 819690.8812; 9 2036: 837724.0806; 10 2037: 856154.0103
|  | Investment year in service |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100
QAQC check |  | 2027 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
3612272.3 |  |  | Book depreciation |  | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 72245.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 3612272.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation |  | -72245.446 | -144490.892 | -216736.338 | -288981.784 | -361227.23 | -433472.676 | -505718.122 | -577963.568 | -650209.014 | -722454.46 | -794699.906 | -866945.352 | -939190.798 | -1011436.244 | -1083681.69 | -1155927.136 | -1228172.582 | -1300418.028 | -1372663.474 | -1444908.92 | -1517154.366 | -1589399.812 | -1661645.258 | -1733890.704 | -1806136.15 | -1878381.596 | -1950627.042 | -2022872.488 | -2095117.934 | -2167363.38 | -2239608.826 | -2311854.272 | -2384099.718 | -2456345.164 | -2528590.61 | -2600836.056 | -2673081.502 | -2745326.948 | -2817572.394 | -2889817.84 | -2962063.286 | -3034308.732 | -3106554.178 | -3178799.624 | -3251045.07 | -3323290.516 | -3395535.962 | -3467781.408 | -3540026.854 | -3612272.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) |  | 3612272.3 | 3540026.854 | 3467781.408 | 3395535.962 | 3323290.516 | 3251045.07 | 3178799.624 | 3106554.178 | 3034308.732 | 2962063.286 | 2889817.84 | 2817572.394 | 2745326.948 | 2673081.502 | 2600836.056 | 2528590.61 | 2456345.164 | 2384099.718 | 2311854.272 | 2239608.826 | 2167363.38 | 2095117.934 | 2022872.488 | 1950627.042 | 1878381.596 | 1806136.15 | 1733890.704 | 1661645.258 | 1589399.812 | 1517154.366 | 1444908.92 | 1372663.474 | 1300418.028 | 1228172.582 | 1155927.136 | 1083681.69 | 1011436.244 | 939190.798 | 866945.352 | 794699.906 | 722454.46 | 650209.014 | 577963.568 | 505718.122 | 433472.676 | 361227.23 | 288981.784 | 216736.338 | 144490.892 | 72245.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) | 3612272.3 | 3540026.854 | 3467781.408 | 3395535.962 | 3323290.516 | 3251045.07 | 3178799.624 | 3106554.178 | 3034308.732 | 2962063.286 | 2889817.84 | 2817572.394 | 2745326.948 | 2673081.502 | 2600836.056 | 2528590.61 | 2456345.164 | 2384099.718 | 2311854.272 | 2239608.826 | 2167363.38 | 2095117.934 | 2022872.488 | 1950627.042 | 1878381.596 | 1806136.15 | 1733890.704 | 1661645.258 | 1589399.812 | 1517154.366 | 1444908.92 | 1372663.474 | 1300418.028 | 1228172.582 | 1155927.136 | 1083681.69 | 1011436.244 | 939190.798 | 866945.352 | 794699.906 | 722454.46 | 650209.014 | 577963.568 | 505718.122 | 433472.676 | 361227.23 | 288981.784 | 216736.338 | 144490.892 | 72245.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation |  | 135460.2112 | 260769.9373 | 241191.4215 | 223130.06 | 206369.1165 | 190908.5911 | 176567.87 | 163346.9534 | 161179.59 | 161143.4673 | 161179.59 | 161143.4673 | 161179.59 | 161143.4673 | 161179.59 | 161143.4673 | 161179.59 | 161143.4673 | 161179.59 | 161143.4673 | 80589.795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) |  | 0 | -17519.9722 | -69769.535 | -116592.9121 | -158410.5828 | -195582.9581 | -228470.4488 | -257383.4086 | -282632.1914 | -307280.2894 | -331918.376 | -356566.474 | -381204.5606 | -405852.6586 | -430490.7452 | -455138.8432 | -479776.9298 | -504425.0279 | -529063.1145 | -553711.2125 | -578349.2991 | -580661.9354 | -560639.11 | -540616.2847 | -520593.4593 | -500570.634 | -480547.8086 | -460524.9833 | -440502.1579 | -420479.3325 | -400456.5072 | -380433.6818 | -360410.8565 | -340388.0311 | -320365.2057 | -300342.3804 | -280319.555 | -260296.7297 | -240273.9043 | -220251.0789 | -200228.2536 | -180205.4282 | -160182.6029 | -140159.7775 | -120136.9522 | -100114.1268 | -80091.3014 | -60068.4761 | -40045.6507 | -20022.8254 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10
|  |  | ADIT (e.o.y.) |  | -17519.9722 | -69769.535 | -116592.9121 | -158410.5828 | -195582.9581 | -228470.4488 | -257383.4086 | -282632.1914 | -307280.2894 | -331918.376 | -356566.474 | -381204.5606 | -405852.6586 | -430490.7452 | -455138.8432 | -479776.9298 | -504425.0279 | -529063.1145 | -553711.2125 | -578349.2991 | -580661.9354 | -560639.11 | -540616.2847 | -520593.4593 | -500570.634 | -480547.8086 | -460524.9833 | -440502.1579 | -420479.3325 | -400456.5072 | -380433.6818 | -360410.8565 | -340388.0311 | -320365.2057 | -300342.3804 | -280319.555 | -260296.7297 | -240273.9043 | -220251.0789 | -200228.2536 | -180205.4282 | -160182.6029 | -140159.7775 | -120136.9522 | -100114.1268 | -80091.3014 | -60068.4761 | -40045.6507 | -20022.8254 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10
|  |  | Net Rate Base |  | 3567389.5909 | 3460259.3774 | 3338477.4615 | 3221911.4916 | 3110171.0225 | 3002895.6436 | 2899749.9723 | 2800423.655 | 2703229.7686 | 2606341.2303 | 2509452.692 | 2412564.1537 | 2315675.6154 | 2218787.0771 | 2121898.5388 | 2025010.0005 | 1928121.4622 | 1831232.9238 | 1734344.3855 | 1637455.8472 | 1551735.0398 | 1488344.6883 | 1436122.0676 | 1383899.447 | 1331676.8263 | 1279454.2057 | 1227231.5851 | 1175008.9644 | 1122786.3438 | 1070563.7231 | 1018341.1025 | 966118.4819 | 913895.8612 | 861673.2406 | 809450.6199 | 757227.9993 | 705005.3787 | 652782.758 | 600560.1374 | 548337.5167 | 496114.8961 | 443892.2754 | 391669.6548 | 339447.0342 | 287224.4135 | 235001.7929 | 182779.1722 | 130556.5516 | 78333.931 | 26111.3103 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10 | 2.2555e-10
|  |  | Pre-Tax return on rate base |  | 318567.8905 | 309001.1624 | 298126.0373 | 287716.6962 | 277738.2723 | 268158.581 | 258947.6725 | 250077.8324 | 241398.4183 | 232746.2719 | 224094.1254 | 215441.9789 | 206789.8325 | 198137.686 | 189485.5395 | 180833.393 | 172181.2466 | 163529.1001 | 154876.9536 | 146224.8072 | 138569.9391 | 132909.1807 | 128245.7006 | 123582.2206 | 118918.7406 | 114255.2606 | 109591.7805 | 104928.3005 | 100264.8205 | 95601.3405 | 90937.8605 | 86274.3804 | 81610.9004 | 76947.4204 | 72283.9404 | 67620.4603 | 62956.9803 | 58293.5003 | 53630.0203 | 48966.5402 | 44303.0602 | 39639.5802 | 34976.1002 | 30312.6202 | 25649.1401 | 20985.6601 | 16322.1801 | 11658.7001 | 6995.22 | 2331.74 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11 | 2.0142e-11
|  | Investment year in service |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99
QAQC check |  | 2028 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
3691742.2906 |  |  | Book depreciation |  |  | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 73834.8458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service |  | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 3691742.2906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation |  |  | -73834.8458 | -147669.6916 | -221504.5374 | -295339.3832 | -369174.2291 | -443009.0749 | -516843.9207 | -590678.7665 | -664513.6123 | -738348.4581 | -812183.3039 | -886018.1497 | -959852.9956 | -1033687.8414 | -1107522.6872 | -1181357.533 | -1255192.3788 | -1329027.2246 | -1402862.0704 | -1476696.9162 | -1550531.7621 | -1624366.6079 | -1698201.4537 | -1772036.2995 | -1845871.1453 | -1919705.9911 | -1993540.8369 | -2067375.6827 | -2141210.5285 | -2215045.3744 | -2288880.2202 | -2362715.066 | -2436549.9118 | -2510384.7576 | -2584219.6034 | -2658054.4492 | -2731889.295 | -2805724.1409 | -2879558.9867 | -2953393.8325 | -3027228.6783 | -3101063.5241 | -3174898.3699 | -3248733.2157 | -3322568.0615 | -3396402.9074 | -3470237.7532 | -3544072.599 | -3617907.4448 | -3691742.2906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) |  |  | 3691742.2906 | 3617907.4448 | 3544072.599 | 3470237.7532 | 3396402.9074 | 3322568.0615 | 3248733.2157 | 3174898.3699 | 3101063.5241 | 3027228.6783 | 2953393.8325 | 2879558.9867 | 2805724.1409 | 2731889.295 | 2658054.4492 | 2584219.6034 | 2510384.7576 | 2436549.9118 | 2362715.066 | 2288880.2202 | 2215045.3744 | 2141210.5285 | 2067375.6827 | 1993540.8369 | 1919705.9911 | 1845871.1453 | 1772036.2995 | 1698201.4537 | 1624366.6079 | 1550531.7621 | 1476696.9162 | 1402862.0704 | 1329027.2246 | 1255192.3788 | 1181357.533 | 1107522.6872 | 1033687.8414 | 959852.9956 | 886018.1497 | 812183.3039 | 738348.4581 | 664513.6123 | 590678.7665 | 516843.9207 | 443009.0749 | 369174.2291 | 295339.3832 | 221504.5374 | 147669.6916 | 73834.8458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) |  | 3691742.2906 | 3617907.4448 | 3544072.599 | 3470237.7532 | 3396402.9074 | 3322568.0615 | 3248733.2157 | 3174898.3699 | 3101063.5241 | 3027228.6783 | 2953393.8325 | 2879558.9867 | 2805724.1409 | 2731889.295 | 2658054.4492 | 2584219.6034 | 2510384.7576 | 2436549.9118 | 2362715.066 | 2288880.2202 | 2215045.3744 | 2141210.5285 | 2067375.6827 | 1993540.8369 | 1919705.9911 | 1845871.1453 | 1772036.2995 | 1698201.4537 | 1624366.6079 | 1550531.7621 | 1476696.9162 | 1402862.0704 | 1329027.2246 | 1255192.3788 | 1181357.533 | 1107522.6872 | 1033687.8414 | 959852.9956 | 886018.1497 | 812183.3039 | 738348.4581 | 664513.6123 | 590678.7665 | 516843.9207 | 443009.0749 | 369174.2291 | 295339.3832 | 221504.5374 | 147669.6916 | 73834.8458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation |  |  | 138440.3359 | 266506.876 | 246497.6327 | 228038.9213 | 210909.2371 | 195108.5801 | 180452.3632 | 166940.5864 | 164725.541 | 164688.6236 | 164725.541 | 164688.6236 | 164725.541 | 164688.6236 | 164725.541 | 164688.6236 | 164725.541 | 164688.6236 | 164725.541 | 164688.6236 | 82362.7705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) |  |  | 0 | -17905.4116 | -71304.4647 | -119157.9561 | -161895.6156 | -199885.7832 | -233496.7986 | -263045.8436 | -288850.0996 | -314040.4557 | -339220.5802 | -364410.9364 | -389591.0609 | -414781.4171 | -439961.5416 | -465151.8978 | -490332.0223 | -515522.3785 | -540702.503 | -565892.8591 | -591072.9837 | -593436.498 | -572973.1705 | -552509.843 | -532046.5154 | -511583.1879 | -491119.8604 | -470656.5329 | -450193.2054 | -429729.8779 | -409266.5503 | -388803.2228 | -368339.8953 | -347876.5678 | -327413.2403 | -306949.9128 | -286486.5852 | -266023.2577 | -245559.9302 | -225096.6027 | -204633.2752 | -184169.9477 | -163706.6201 | -143243.2926 | -122779.9651 | -102316.6376 | -81853.3101 | -61389.9826 | -40926.655 | -20463.3275 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10
|  |  | ADIT (e.o.y.) |  |  | -17905.4116 | -71304.4647 | -119157.9561 | -161895.6156 | -199885.7832 | -233496.7986 | -263045.8436 | -288850.0996 | -314040.4557 | -339220.5802 | -364410.9364 | -389591.0609 | -414781.4171 | -439961.5416 | -465151.8978 | -490332.0223 | -515522.3785 | -540702.503 | -565892.8591 | -591072.9837 | -593436.498 | -572973.1705 | -552509.843 | -532046.5154 | -511583.1879 | -491119.8604 | -470656.5329 | -450193.2054 | -429729.8779 | -409266.5503 | -388803.2228 | -368339.8953 | -347876.5678 | -327413.2403 | -306949.9128 | -286486.5852 | -266023.2577 | -245559.9302 | -225096.6027 | -204633.2752 | -184169.9477 | -163706.6201 | -143243.2926 | -122779.9651 | -102316.6376 | -81853.3101 | -61389.9826 | -40926.655 | -20463.3275 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10
|  |  | Net Rate Base |  |  | 3645872.1619 | 3536385.0837 | 3411923.9656 | 3292793.5444 | 3178594.785 | 3068959.3477 | 2963544.4717 | 2862032.9754 | 2762700.8235 | 2663680.7374 | 2564660.6512 | 2465640.5651 | 2366620.4789 | 2267600.3928 | 2168580.3066 | 2069560.2205 | 1970540.1343 | 1871520.0482 | 1772499.962 | 1673479.8759 | 1585873.2106 | 1521088.2714 | 1467716.7531 | 1414345.2348 | 1360973.7165 | 1307602.1982 | 1254230.6799 | 1200859.1616 | 1147487.6433 | 1094116.1251 | 1040744.6068 | 987373.0885 | 934001.5702 | 880630.0519 | 827258.5336 | 773887.0153 | 720515.497 | 667143.9787 | 613772.4604 | 560400.9421 | 507029.4238 | 453657.9055 | 400286.3872 | 346914.8689 | 293543.3506 | 240171.8323 | 186800.314 | 133428.7957 | 80057.2774 | 26685.7591 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10 | 6.6939e-10
|  |  | Pre-Tax return on rate base |  |  | 325576.3841 | 315799.188 | 304684.8101 | 294046.4635 | 283848.5143 | 274058.0698 | 264644.5213 | 255579.5447 | 246709.1835 | 237866.6898 | 229024.1962 | 220181.7025 | 211339.2088 | 202496.7151 | 193654.2214 | 184811.7277 | 175969.234 | 167126.7403 | 158284.2466 | 149441.7529 | 141618.4777 | 135833.1826 | 131067.1061 | 126301.0295 | 121534.9529 | 116768.8763 | 112002.7997 | 107236.7231 | 102470.6466 | 97704.57 | 92938.4934 | 88172.4168 | 83406.3402 | 78640.2636 | 73874.187 | 69108.1105 | 64342.0339 | 59575.9573 | 54809.8807 | 50043.8041 | 45277.7275 | 40511.651 | 35745.5744 | 30979.4978 | 26213.4212 | 21447.3446 | 16681.268 | 11915.1915 | 7149.1149 | 2383.0383 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11 | 5.9776e-11
|  | Investment year in service |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98
QAQC check |  | 2029 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
3772960.621 |  |  | Book depreciation |  |  |  | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 75459.2124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service |  |  | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 3772960.621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation |  |  |  | -75459.2124 | -150918.4248 | -226377.6373 | -301836.8497 | -377296.0621 | -452755.2745 | -528214.4869 | -603673.6994 | -679132.9118 | -754592.1242 | -830051.3366 | -905510.549 | -980969.7615 | -1056428.9739 | -1131888.1863 | -1207347.3987 | -1282806.6111 | -1358265.8236 | -1433725.036 | -1509184.2484 | -1584643.4608 | -1660102.6732 | -1735561.8857 | -1811021.0981 | -1886480.3105 | -1961939.5229 | -2037398.7353 | -2112857.9478 | -2188317.1602 | -2263776.3726 | -2339235.585 | -2414694.7974 | -2490154.0099 | -2565613.2223 | -2641072.4347 | -2716531.6471 | -2791990.8595 | -2867450.072 | -2942909.2844 | -3018368.4968 | -3093827.7092 | -3169286.9216 | -3244746.1341 | -3320205.3465 | -3395664.5589 | -3471123.7713 | -3546582.9837 | -3622042.1962 | -3697501.4086 | -3772960.621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) |  |  |  | 3772960.621 | 3697501.4086 | 3622042.1962 | 3546582.9837 | 3471123.7713 | 3395664.5589 | 3320205.3465 | 3244746.1341 | 3169286.9216 | 3093827.7092 | 3018368.4968 | 2942909.2844 | 2867450.072 | 2791990.8595 | 2716531.6471 | 2641072.4347 | 2565613.2223 | 2490154.0099 | 2414694.7974 | 2339235.585 | 2263776.3726 | 2188317.1602 | 2112857.9478 | 2037398.7353 | 1961939.5229 | 1886480.3105 | 1811021.0981 | 1735561.8857 | 1660102.6732 | 1584643.4608 | 1509184.2484 | 1433725.036 | 1358265.8236 | 1282806.6111 | 1207347.3987 | 1131888.1863 | 1056428.9739 | 980969.7615 | 905510.549 | 830051.3366 | 754592.1242 | 679132.9118 | 603673.6994 | 528214.4869 | 452755.2745 | 377296.0621 | 301836.8497 | 226377.6373 | 150918.4248 | 75459.2124 | 4.6566e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) |  |  | 3772960.621 | 3697501.4086 | 3622042.1962 | 3546582.9837 | 3471123.7713 | 3395664.5589 | 3320205.3465 | 3244746.1341 | 3169286.9216 | 3093827.7092 | 3018368.4968 | 2942909.2844 | 2867450.072 | 2791990.8595 | 2716531.6471 | 2641072.4347 | 2565613.2223 | 2490154.0099 | 2414694.7974 | 2339235.585 | 2263776.3726 | 2188317.1602 | 2112857.9478 | 2037398.7353 | 1961939.5229 | 1886480.3105 | 1811021.0981 | 1735561.8857 | 1660102.6732 | 1584643.4608 | 1509184.2484 | 1433725.036 | 1358265.8236 | 1282806.6111 | 1207347.3987 | 1131888.1863 | 1056428.9739 | 980969.7615 | 905510.549 | 830051.3366 | 754592.1242 | 679132.9118 | 603673.6994 | 528214.4869 | 452755.2745 | 377296.0621 | 301836.8497 | 226377.6373 | 150918.4248 | 75459.2124 | 4.6566e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation |  |  |  | 141486.0233 | 272370.0272 | 251920.5807 | 233055.7776 | 215549.2403 | 199400.9688 | 184422.3152 | 170613.2793 | 168349.5029 | 168311.7733 | 168349.5029 | 168311.7733 | 168349.5029 | 168311.7733 | 168349.5029 | 168311.7733 | 168349.5029 | 168311.7733 | 168349.5029 | 168311.7733 | 84174.7515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) |  |  |  | 0 | -18299.3306 | -72873.163 | -121779.4312 | -165457.3192 | -204283.2704 | -238633.7282 | -268832.8521 | -295204.8018 | -320949.3458 | -346683.433 | -372427.977 | -398162.0643 | -423906.6083 | -449640.6955 | -475385.2395 | -501119.3268 | -526863.8708 | -552597.958 | -578342.5021 | -604076.5893 | -606492.1009 | -585578.5802 | -564665.0595 | -543751.5388 | -522838.0181 | -501924.4973 | -481010.9766 | -460097.4559 | -439183.9352 | -418270.4144 | -397356.8937 | -376443.373 | -355529.8523 | -334616.3316 | -313702.8108 | -292789.2901 | -271875.7694 | -250962.2487 | -230048.7279 | -209135.2072 | -188221.6865 | -167308.1658 | -146394.6451 | -125481.1243 | -104567.6036 | -83654.0829 | -62740.5622 | -41827.0414 | -20913.5207 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10
|  |  | ADIT (e.o.y.) |  |  |  | -18299.3306 | -72873.163 | -121779.4312 | -165457.3192 | -204283.2704 | -238633.7282 | -268832.8521 | -295204.8018 | -320949.3458 | -346683.433 | -372427.977 | -398162.0643 | -423906.6083 | -449640.6955 | -475385.2395 | -501119.3268 | -526863.8708 | -552597.958 | -578342.5021 | -604076.5893 | -606492.1009 | -585578.5802 | -564665.0595 | -543751.5388 | -522838.0181 | -501924.4973 | -481010.9766 | -460097.4559 | -439183.9352 | -418270.4144 | -397356.8937 | -376443.373 | -355529.8523 | -334616.3316 | -313702.8108 | -292789.2901 | -271875.7694 | -250962.2487 | -230048.7279 | -209135.2072 | -188221.6865 | -167308.1658 | -146394.6451 | -125481.1243 | -104567.6036 | -83654.0829 | -62740.5622 | -41827.0414 | -20913.5207 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10
|  |  | Net Rate Base |  |  |  | 3726081.3495 | 3614185.5556 | 3486986.2929 | 3365235.0023 | 3248523.8703 | 3136476.4534 | 3028742.4501 | 2924997.7009 | 2823480.2417 | 2722281.7136 | 2621083.1856 | 2519884.6575 | 2418686.1295 | 2317487.6014 | 2216289.0734 | 2115090.5453 | 2013892.0173 | 1912693.4892 | 1811494.9612 | 1710296.4331 | 1620762.4213 | 1554552.2134 | 1500006.5217 | 1445460.83 | 1390915.1383 | 1336369.4466 | 1281823.7549 | 1227278.0632 | 1172732.3715 | 1118186.6798 | 1063640.9881 | 1009095.2964 | 954549.6047 | 900003.913 | 845458.2213 | 790912.5296 | 736366.8379 | 681821.1462 | 627275.4545 | 572729.7628 | 518184.0711 | 463638.3794 | 409092.6877 | 354546.996 | 300001.3043 | 245455.6126 | 190909.9209 | 136364.2292 | 81818.5375 | 27272.8458 | 2.1973e-09 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10 | -1.3097e-10
|  |  | Pre-Tax return on rate base |  |  |  | 332739.0645 | 322746.7701 | 311387.876 | 300515.4857 | 290093.1816 | 280087.3473 | 270466.7008 | 261202.2947 | 252136.7856 | 243099.757 | 234062.7285 | 225025.6999 | 215988.6714 | 206951.6428 | 197914.6143 | 188877.5857 | 179840.5571 | 170803.5286 | 161766.5 | 152729.4715 | 144734.0842 | 138821.5127 | 133950.5824 | 129079.6521 | 124208.7218 | 119337.7916 | 114466.8613 | 109595.931 | 104725.0008 | 99854.0705 | 94983.1402 | 90112.21 | 85241.2797 | 80370.3494 | 75499.4192 | 70628.4889 | 65757.5586 | 60886.6284 | 56015.6981 | 51144.7678 | 46273.8376 | 41402.9073 | 36531.977 | 31661.0467 | 26790.1165 | 21919.1862 | 17048.2559 | 12177.3257 | 7306.3954 | 2435.4651 | 1.9622e-10 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11 | -1.1695e-11
|  | Investment year in service |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97
|  | 2030 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
|  |  | Book depreciation |  |  |  |  | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 77119.3151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service |  |  |  | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 3855965.7547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation |  |  |  |  | -77119.3151 | -154238.6302 | -231357.9453 | -308477.2604 | -385596.5755 | -462715.8906 | -539835.2057 | -616954.5207 | -694073.8358 | -771193.1509 | -848312.466 | -925431.7811 | -1002551.0962 | -1079670.4113 | -1156789.7264 | -1233909.0415 | -1311028.3566 | -1388147.6717 | -1465266.9868 | -1542386.3019 | -1619505.617 | -1696624.932 | -1773744.2471 | -1850863.5622 | -1927982.8773 | -2005102.1924 | -2082221.5075 | -2159340.8226 | -2236460.1377 | -2313579.4528 | -2390698.7679 | -2467818.083 | -2544937.3981 | -2622056.7132 | -2699176.0283 | -2776295.3434 | -2853414.6584 | -2930533.9735 | -3007653.2886 | -3084772.6037 | -3161891.9188 | -3239011.2339 | -3316130.549 | -3393249.8641 | -3470369.1792 | -3547488.4943 | -3624607.8094 | -3701727.1245 | -3778846.4396 | -3855965.7547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) |  |  |  |  | 3855965.7547 | 3778846.4396 | 3701727.1245 | 3624607.8094 | 3547488.4943 | 3470369.1792 | 3393249.8641 | 3316130.549 | 3239011.2339 | 3161891.9188 | 3084772.6037 | 3007653.2886 | 2930533.9735 | 2853414.6584 | 2776295.3434 | 2699176.0283 | 2622056.7132 | 2544937.3981 | 2467818.083 | 2390698.7679 | 2313579.4528 | 2236460.1377 | 2159340.8226 | 2082221.5075 | 2005102.1924 | 1927982.8773 | 1850863.5622 | 1773744.2471 | 1696624.932 | 1619505.617 | 1542386.3019 | 1465266.9868 | 1388147.6717 | 1311028.3566 | 1233909.0415 | 1156789.7264 | 1079670.4113 | 1002551.0962 | 925431.7811 | 848312.466 | 771193.1509 | 694073.8358 | 616954.5207 | 539835.2057 | 462715.8906 | 385596.5755 | 308477.2604 | 231357.9453 | 154238.6302 | 77119.3151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) |  |  |  | 3855965.7547 | 3778846.4396 | 3701727.1245 | 3624607.8094 | 3547488.4943 | 3470369.1792 | 3393249.8641 | 3316130.549 | 3239011.2339 | 3161891.9188 | 3084772.6037 | 3007653.2886 | 2930533.9735 | 2853414.6584 | 2776295.3434 | 2699176.0283 | 2622056.7132 | 2544937.3981 | 2467818.083 | 2390698.7679 | 2313579.4528 | 2236460.1377 | 2159340.8226 | 2082221.5075 | 2005102.1924 | 1927982.8773 | 1850863.5622 | 1773744.2471 | 1696624.932 | 1619505.617 | 1542386.3019 | 1465266.9868 | 1388147.6717 | 1311028.3566 | 1233909.0415 | 1156789.7264 | 1079670.4113 | 1002551.0962 | 925431.7811 | 848312.466 | 771193.1509 | 694073.8358 | 616954.5207 | 539835.2057 | 462715.8906 | 385596.5755 | 308477.2604 | 231357.9453 | 154238.6302 | 77119.3151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation |  |  |  |  | 144598.7158 | 278362.1678 | 257462.8334 | 238183.0047 | 220291.3236 | 203787.7901 | 188479.6061 | 174366.7714 | 172053.192 | 172014.6323 | 172053.192 | 172014.6323 | 172053.192 | 172014.6323 | 172053.192 | 172014.6323 | 172053.192 | 172014.6323 | 172053.192 | 172014.6323 | 86026.596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) |  |  |  |  | 0 | -18701.9159 | -74476.3725 | -124458.5787 | -169097.3802 | -208777.5024 | -243883.6702 | -274747.1749 | -301699.3074 | -328010.2314 | -354310.4685 | -380621.3925 | -406921.6297 | -433232.5537 | -459532.7908 | -485843.7148 | -512143.952 | -538454.876 | -564755.1131 | -591066.0371 | -617366.2743 | -619834.9272 | -598461.309 | -577087.6908 | -555714.0726 | -534340.4545 | -512966.8363 | -491593.2181 | -470219.5999 | -448845.9817 | -427472.3636 | -406098.7454 | -384725.1272 | -363351.509 | -341977.8908 | -320604.2727 | -299230.6545 | -277857.0363 | -256483.4181 | -235109.8 | -213736.1818 | -192362.5636 | -170988.9454 | -149615.3272 | -128241.7091 | -106868.0909 | -85494.4727 | -64120.8545 | -42747.2364 | -21373.6182 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10
|  |  | ADIT (e.o.y.) |  |  |  |  | -18701.9159 | -74476.3725 | -124458.5787 | -169097.3802 | -208777.5024 | -243883.6702 | -274747.1749 | -301699.3074 | -328010.2314 | -354310.4685 | -380621.3925 | -406921.6297 | -433232.5537 | -459532.7908 | -485843.7148 | -512143.952 | -538454.876 | -564755.1131 | -591066.0371 | -617366.2743 | -619834.9272 | -598461.309 | -577087.6908 | -555714.0726 | -534340.4545 | -512966.8363 | -491593.2181 | -470219.5999 | -448845.9817 | -427472.3636 | -406098.7454 | -384725.1272 | -363351.509 | -341977.8908 | -320604.2727 | -299230.6545 | -277857.0363 | -256483.4181 | -235109.8 | -213736.1818 | -192362.5636 | -170988.9454 | -149615.3272 | -128241.7091 | -106868.0909 | -85494.4727 | -64120.8545 | -42747.2364 | -21373.6182 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10
|  |  | Net Rate Base |  |  |  |  | 3808055.1392 | 3693697.6378 | 3563699.9913 | 3439270.1724 | 3319991.3954 | 3205478.9354 | 3095374.784 | 2989347.6503 | 2885596.807 | 2782171.9113 | 2678747.0157 | 2575322.12 | 2471897.2243 | 2368472.3287 | 2265047.433 | 2161622.5373 | 2058197.6417 | 1954772.746 | 1851347.8503 | 1747922.9547 | 1656419.1945 | 1588752.3621 | 1533006.6652 | 1477260.9682 | 1421515.2713 | 1365769.5744 | 1310023.8775 | 1254278.1806 | 1198532.4837 | 1142786.7868 | 1087041.0898 | 1031295.3929 | 975549.696 | 919803.9991 | 864058.3022 | 808312.6053 | 752566.9084 | 696821.2114 | 641075.5145 | 585329.8176 | 529584.1207 | 473838.4238 | 418092.7269 | 362347.0299 | 306601.333 | 250855.6361 | 195109.9392 | 139364.2423 | 83618.5454 | 27872.8485 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10 | 1.2369e-10
|  |  | Pre-Tax return on rate base |  |  |  |  | 340059.3239 | 329847.1991 | 318238.4092 | 307126.8264 | 296475.2316 | 286249.2689 | 276416.9682 | 266948.7452 | 257683.7949 | 248447.9517 | 239212.1085 | 229976.2653 | 220740.4221 | 211504.5789 | 202268.7358 | 193032.8926 | 183797.0494 | 174561.2062 | 165325.363 | 156089.5199 | 147918.2341 | 141875.5859 | 136897.4952 | 131919.4045 | 126941.3137 | 121963.223 | 116985.1323 | 112007.0415 | 107028.9508 | 102050.8601 | 97072.7693 | 92094.6786 | 87116.5879 | 82138.4971 | 77160.4064 | 72182.3157 | 67204.2249 | 62226.1342 | 57248.0434 | 52269.9527 | 47291.862 | 42313.7712 | 37335.6805 | 32357.5898 | 27379.499 | 22401.4083 | 17423.3176 | 12445.2268 | 7467.1361 | 2489.0454 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11 | 1.1046e-11
|  | Investment year in service | [5 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96
|  | 2031 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
|  |  | Book depreciation | [5 empty] | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 78815.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service |  |  |  |  | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 3940797.0013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation | [5 empty] | -78815.94 | -157631.8801 | -236447.8201 | -315263.7601 | -394079.7001 | -472895.6402 | -551711.5802 | -630527.5202 | -709343.4602 | -788159.4003 | -866975.3403 | -945791.2803 | -1024607.2203 | -1103423.1604 | -1182239.1004 | -1261055.0404 | -1339870.9804 | -1418686.9205 | -1497502.8605 | -1576318.8005 | -1655134.7405 | -1733950.6806 | -1812766.6206 | -1891582.5606 | -1970398.5006 | -2049214.4407 | -2128030.3807 | -2206846.3207 | -2285662.2607 | -2364478.2008 | -2443294.1408 | -2522110.0808 | -2600926.0208 | -2679741.9609 | -2758557.9009 | -2837373.8409 | -2916189.7809 | -2995005.721 | -3073821.661 | -3152637.601 | -3231453.541 | -3310269.4811 | -3389085.4211 | -3467901.3611 | -3546717.3011 | -3625533.2412 | -3704349.1812 | -3783165.1212 | -3861981.0612 | -3940797.0013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) | [5 empty] | 3940797.0013 | 3861981.0612 | 3783165.1212 | 3704349.1812 | 3625533.2412 | 3546717.3011 | 3467901.3611 | 3389085.4211 | 3310269.4811 | 3231453.541 | 3152637.601 | 3073821.661 | 2995005.721 | 2916189.7809 | 2837373.8409 | 2758557.9009 | 2679741.9609 | 2600926.0208 | 2522110.0808 | 2443294.1408 | 2364478.2008 | 2285662.2607 | 2206846.3207 | 2128030.3807 | 2049214.4407 | 1970398.5006 | 1891582.5606 | 1812766.6206 | 1733950.6806 | 1655134.7405 | 1576318.8005 | 1497502.8605 | 1418686.9205 | 1339870.9804 | 1261055.0404 | 1182239.1004 | 1103423.1604 | 1024607.2203 | 945791.2803 | 866975.3403 | 788159.4003 | 709343.4602 | 630527.5202 | 551711.5802 | 472895.6402 | 394079.7001 | 315263.7601 | 236447.8201 | 157631.8801 | 78815.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) |  |  |  |  | 3940797.0013 | 3861981.0612 | 3783165.1212 | 3704349.1812 | 3625533.2412 | 3546717.3011 | 3467901.3611 | 3389085.4211 | 3310269.4811 | 3231453.541 | 3152637.601 | 3073821.661 | 2995005.721 | 2916189.7809 | 2837373.8409 | 2758557.9009 | 2679741.9609 | 2600926.0208 | 2522110.0808 | 2443294.1408 | 2364478.2008 | 2285662.2607 | 2206846.3207 | 2128030.3807 | 2049214.4407 | 1970398.5006 | 1891582.5606 | 1812766.6206 | 1733950.6806 | 1655134.7405 | 1576318.8005 | 1497502.8605 | 1418686.9205 | 1339870.9804 | 1261055.0404 | 1182239.1004 | 1103423.1604 | 1024607.2203 | 945791.2803 | 866975.3403 | 788159.4003 | 709343.4602 | 630527.5202 | 551711.5802 | 472895.6402 | 394079.7001 | 315263.7601 | 236447.8201 | 157631.8801 | 78815.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation | [5 empty] | 147779.8875 | 284486.1355 | 263127.0158 | 243423.0308 | 225137.7327 | 208271.1215 | 192626.1574 | 178202.8404 | 175838.3622 | 175798.9542 | 175838.3622 | 175798.9542 | 175838.3622 | 175798.9542 | 175838.3622 | 175798.9542 | 175838.3622 | 175798.9542 | 175838.3622 | 175798.9542 | 87919.1811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) | [5 empty] | 0 | -19113.3581 | -76114.8527 | -127196.6674 | -172817.5226 | -213370.6074 | -249249.111 | -280791.6127 | -308336.6922 | -335226.4565 | -362105.2988 | -388995.0632 | -415873.9055 | -442763.6698 | -469642.5122 | -496532.2765 | -523411.1189 | -550300.8832 | -577179.7256 | -604069.4899 | -630948.3323 | -633471.2956 | -611627.4578 | -589783.62 | -567939.7822 | -546095.9444 | -524252.1067 | -502408.2689 | -480564.4311 | -458720.5933 | -436876.7556 | -415032.9178 | -393189.08 | -371345.2422 | -349501.4044 | -327657.5667 | -305813.7289 | -283969.8911 | -262126.0533 | -240282.2156 | -218438.3778 | -196594.54 | -174750.7022 | -152906.8644 | -131063.0267 | -109219.1889 | -87375.3511 | -65531.5133 | -43687.6756 | -21843.8378 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10
|  |  | ADIT (e.o.y.) | [5 empty] | -19113.3581 | -76114.8527 | -127196.6674 | -172817.5226 | -213370.6074 | -249249.111 | -280791.6127 | -308336.6922 | -335226.4565 | -362105.2988 | -388995.0632 | -415873.9055 | -442763.6698 | -469642.5122 | -496532.2765 | -523411.1189 | -550300.8832 | -577179.7256 | -604069.4899 | -630948.3323 | -633471.2956 | -611627.4578 | -589783.62 | -567939.7822 | -546095.9444 | -524252.1067 | -502408.2689 | -480564.4311 | -458720.5933 | -436876.7556 | -415032.9178 | -393189.08 | -371345.2422 | -349501.4044 | -327657.5667 | -305813.7289 | -283969.8911 | -262126.0533 | -240282.2156 | -218438.3778 | -196594.54 | -174750.7022 | -152906.8644 | -131063.0267 | -109219.1889 | -87375.3511 | -65531.5133 | -43687.6756 | -21843.8378 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10
|  |  | Net Rate Base | [5 empty] | 3891832.3522 | 3774958.9858 | 3642101.3911 | 3514934.1162 | 3393031.2061 | 3275999.4719 | 3163473.0293 | 3055113.2986 | 2949079.9367 | 2843379.6934 | 2737679.45 | 2631979.2066 | 2526278.9633 | 2420578.7199 | 2314878.4765 | 2209178.2331 | 2103477.9898 | 1997777.7464 | 1892077.503 | 1786377.2597 | 1692860.4168 | 1623704.914 | 1566732.8118 | 1509760.7096 | 1452788.6073 | 1395816.5051 | 1338844.4028 | 1281872.3006 | 1224900.1983 | 1167928.0961 | 1110955.9938 | 1053983.8916 | 997011.7893 | 940039.6871 | 883067.5848 | 826095.4826 | 769123.3803 | 712151.2781 | 655179.1758 | 598207.0736 | 541234.9713 | 484262.8691 | 427290.7669 | 370318.6646 | 313346.5624 | 256374.4601 | 199402.3579 | 142430.2556 | 85458.1534 | 28486.0511 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10 | 3.638e-10
|  |  | Pre-Tax return on rate base | [5 empty] | 347540.6291 | 337103.8374 | 325239.6542 | 313883.6166 | 302997.6867 | 292546.7528 | 282498.1415 | 272821.6176 | 263352.8384 | 253913.8066 | 244474.7749 | 235035.7432 | 225596.7114 | 216157.6797 | 206718.648 | 197279.6162 | 187840.5845 | 178401.5528 | 168962.521 | 159523.4893 | 151172.4352 | 144996.8488 | 139909.2401 | 134821.6314 | 129734.0226 | 124646.4139 | 119558.8052 | 114471.1964 | 109383.5877 | 104295.979 | 99208.3702 | 94120.7615 | 89033.1528 | 83945.5441 | 78857.9353 | 73770.3266 | 68682.7179 | 63595.1091 | 58507.5004 | 53419.8917 | 48332.2829 | 43244.6742 | 38157.0655 | 33069.4567 | 27981.848 | 22894.2393 | 17806.6306 | 12719.0218 | 7631.4131 | 2543.8044 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11 | 3.2487e-11
|  | Investment year in service | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95
|  | 2032 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
|  |  | Book depreciation | [6 empty] | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 80549.8907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service | [5 empty] | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 4027494.5353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation | [6 empty] | -80549.8907 | -161099.7814 | -241649.6721 | -322199.5628 | -402749.4535 | -483299.3442 | -563849.2349 | -644399.1256 | -724949.0164 | -805498.9071 | -886048.7978 | -966598.6885 | -1047148.5792 | -1127698.4699 | -1208248.3606 | -1288798.2513 | -1369348.142 | -1449898.0327 | -1530447.9234 | -1610997.8141 | -1691547.7048 | -1772097.5955 | -1852647.4862 | -1933197.3769 | -2013747.2676 | -2094297.1583 | -2174847.0491 | -2255396.9398 | -2335946.8305 | -2416496.7212 | -2497046.6119 | -2577596.5026 | -2658146.3933 | -2738696.284 | -2819246.1747 | -2899796.0654 | -2980345.9561 | -3060895.8468 | -3141445.7375 | -3221995.6282 | -3302545.5189 | -3383095.4096 | -3463645.3003 | -3544195.1911 | -3624745.0818 | -3705294.9725 | -3785844.8632 | -3866394.7539 | -3946944.6446 | -4027494.5353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) | [6 empty] | 4027494.5353 | 3946944.6446 | 3866394.7539 | 3785844.8632 | 3705294.9725 | 3624745.0818 | 3544195.1911 | 3463645.3003 | 3383095.4096 | 3302545.5189 | 3221995.6282 | 3141445.7375 | 3060895.8468 | 2980345.9561 | 2899796.0654 | 2819246.1747 | 2738696.284 | 2658146.3933 | 2577596.5026 | 2497046.6119 | 2416496.7212 | 2335946.8305 | 2255396.9398 | 2174847.0491 | 2094297.1583 | 2013747.2676 | 1933197.3769 | 1852647.4862 | 1772097.5955 | 1691547.7048 | 1610997.8141 | 1530447.9234 | 1449898.0327 | 1369348.142 | 1288798.2513 | 1208248.3606 | 1127698.4699 | 1047148.5792 | 966598.6885 | 886048.7978 | 805498.9071 | 724949.0164 | 644399.1256 | 563849.2349 | 483299.3442 | 402749.4535 | 322199.5628 | 241649.6721 | 161099.7814 | 80549.8907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) | [5 empty] | 4027494.5353 | 3946944.6446 | 3866394.7539 | 3785844.8632 | 3705294.9725 | 3624745.0818 | 3544195.1911 | 3463645.3003 | 3383095.4096 | 3302545.5189 | 3221995.6282 | 3141445.7375 | 3060895.8468 | 2980345.9561 | 2899796.0654 | 2819246.1747 | 2738696.284 | 2658146.3933 | 2577596.5026 | 2497046.6119 | 2416496.7212 | 2335946.8305 | 2255396.9398 | 2174847.0491 | 2094297.1583 | 2013747.2676 | 1933197.3769 | 1852647.4862 | 1772097.5955 | 1691547.7048 | 1610997.8141 | 1530447.9234 | 1449898.0327 | 1369348.142 | 1288798.2513 | 1208248.3606 | 1127698.4699 | 1047148.5792 | 966598.6885 | 886048.7978 | 805498.9071 | 724949.0164 | 644399.1256 | 563849.2349 | 483299.3442 | 402749.4535 | 322199.5628 | 241649.6721 | 161099.7814 | 80549.8907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation | [6 empty] | 151031.0451 | 290744.8305 | 268915.8101 | 248778.3374 | 230090.7628 | 212853.0862 | 196863.9329 | 182123.3029 | 179706.8062 | 179666.5312 | 179706.8062 | 179666.5312 | 179706.8062 | 179666.5312 | 179706.8062 | 179666.5312 | 179706.8062 | 179666.5312 | 179706.8062 | 179666.5312 | 89853.4031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) | [6 empty] | 0 | -19533.8519 | -77789.3795 | -129994.9941 | -176619.5081 | -218064.7608 | -254732.5914 | -286969.0282 | -315120.0994 | -342601.4385 | -370071.6154 | -397552.9545 | -425023.1315 | -452504.4706 | -479974.6475 | -507455.9866 | -534926.1635 | -562407.5027 | -589877.6796 | -617359.0187 | -644829.1956 | -647407.6641 | -625083.2619 | -602758.8596 | -580434.4574 | -558110.0552 | -535785.653 | -513461.2508 | -491136.8486 | -468812.4464 | -446488.0442 | -424163.642 | -401839.2398 | -379514.8376 | -357190.4353 | -334866.0331 | -312541.6309 | -290217.2287 | -267892.8265 | -245568.4243 | -223244.0221 | -200919.6199 | -178595.2177 | -156270.8155 | -133946.4133 | -111622.011 | -89297.6088 | -66973.2066 | -44648.8044 | -22324.4022 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10
|  |  | ADIT (e.o.y.) | [6 empty] | -19533.8519 | -77789.3795 | -129994.9941 | -176619.5081 | -218064.7608 | -254732.5914 | -286969.0282 | -315120.0994 | -342601.4385 | -370071.6154 | -397552.9545 | -425023.1315 | -452504.4706 | -479974.6475 | -507455.9866 | -534926.1635 | -562407.5027 | -589877.6796 | -617359.0187 | -644829.1956 | -647407.6641 | -625083.2619 | -602758.8596 | -580434.4574 | -558110.0552 | -535785.653 | -513461.2508 | -491136.8486 | -468812.4464 | -446488.0442 | -424163.642 | -401839.2398 | -379514.8376 | -357190.4353 | -334866.0331 | -312541.6309 | -290217.2287 | -267892.8265 | -245568.4243 | -223244.0221 | -200919.6199 | -178595.2177 | -156270.8155 | -133946.4133 | -111622.011 | -89297.6088 | -66973.2066 | -44648.8044 | -22324.4022 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10
|  |  | Net Rate Base | [6 empty] | 3977452.664 | 3858008.0835 | 3722227.6217 | 3592262.6667 | 3467677.8927 | 3348071.4603 | 3233069.4359 | 3122325.7912 | 3013959.6953 | 2905934.0466 | 2797908.3979 | 2689882.7492 | 2581857.1004 | 2473831.4517 | 2365805.803 | 2257780.1543 | 2149754.5055 | 2041728.8568 | 1933703.2081 | 1825677.5594 | 1730103.346 | 1659426.4222 | 1601200.9337 | 1542975.4452 | 1484749.9567 | 1426524.4682 | 1368298.9797 | 1310073.4912 | 1251848.0027 | 1193622.5142 | 1135397.0257 | 1077171.5372 | 1018946.0487 | 960720.5602 | 902495.0717 | 844269.5832 | 786044.0947 | 727818.6062 | 669593.1177 | 611367.6292 | 553142.1407 | 494916.6522 | 436691.1637 | 378465.6752 | 320240.1867 | 262014.6982 | 203789.2097 | 145563.7212 | 87338.2327 | 29112.7442 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10 | 2.6193e-10
|  |  | Pre-Tax return on rate base | [6 empty] | 355186.5229 | 344520.1219 | 332394.9266 | 320789.0561 | 309663.6358 | 298982.7814 | 288713.1006 | 278823.6932 | 269146.6008 | 259499.9104 | 249853.2199 | 240206.5295 | 230559.8391 | 220913.1486 | 211266.4582 | 201619.7678 | 191973.0773 | 182326.3869 | 172679.6965 | 163033.0061 | 154498.2288 | 148186.7795 | 142987.2434 | 137787.7073 | 132588.1711 | 127388.635 | 122189.0989 | 116989.5628 | 111790.0266 | 106590.4905 | 101390.9544 | 96191.4183 | 90991.8821 | 85792.346 | 80592.8099 | 75393.2738 | 70193.7377 | 64994.2015 | 59794.6654 | 54595.1293 | 49395.5932 | 44196.057 | 38996.5209 | 33796.9848 | 28597.4487 | 23397.9126 | 18198.3764 | 12998.8403 | 7799.3042 | 2599.7681 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11 | 2.3391e-11
|  | Investment year in service | [7 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94
|  | 2033 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
|  |  | Book depreciation | [7 empty] | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 82321.9883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service | [6 empty] | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 4116099.4151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation | [7 empty] | -82321.9883 | -164643.9766 | -246965.9649 | -329287.9532 | -411609.9415 | -493931.9298 | -576253.9181 | -658575.9064 | -740897.8947 | -823219.883 | -905541.8713 | -987863.8596 | -1070185.8479 | -1152507.8362 | -1234829.8245 | -1317151.8128 | -1399473.8011 | -1481795.7894 | -1564117.7777 | -1646439.766 | -1728761.7543 | -1811083.7426 | -1893405.7309 | -1975727.7192 | -2058049.7075 | -2140371.6958 | -2222693.6841 | -2305015.6724 | -2387337.6607 | -2469659.649 | -2551981.6373 | -2634303.6256 | -2716625.6139 | -2798947.6022 | -2881269.5905 | -2963591.5788 | -3045913.5671 | -3128235.5554 | -3210557.5437 | -3292879.532 | -3375201.5204 | -3457523.5087 | -3539845.497 | -3622167.4853 | -3704489.4736 | -3786811.4619 | -3869133.4502 | -3951455.4385 | -4033777.4268 | -4116099.4151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) | [7 empty] | 4116099.4151 | 4033777.4268 | 3951455.4385 | 3869133.4502 | 3786811.4619 | 3704489.4736 | 3622167.4853 | 3539845.497 | 3457523.5087 | 3375201.5204 | 3292879.532 | 3210557.5437 | 3128235.5554 | 3045913.5671 | 2963591.5788 | 2881269.5905 | 2798947.6022 | 2716625.6139 | 2634303.6256 | 2551981.6373 | 2469659.649 | 2387337.6607 | 2305015.6724 | 2222693.6841 | 2140371.6958 | 2058049.7075 | 1975727.7192 | 1893405.7309 | 1811083.7426 | 1728761.7543 | 1646439.766 | 1564117.7777 | 1481795.7894 | 1399473.8011 | 1317151.8128 | 1234829.8245 | 1152507.8362 | 1070185.8479 | 987863.8596 | 905541.8713 | 823219.883 | 740897.8947 | 658575.9064 | 576253.9181 | 493931.9298 | 411609.9415 | 329287.9532 | 246965.9649 | 164643.9766 | 82321.9883 | 3.7253e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) | [6 empty] | 4116099.4151 | 4033777.4268 | 3951455.4385 | 3869133.4502 | 3786811.4619 | 3704489.4736 | 3622167.4853 | 3539845.497 | 3457523.5087 | 3375201.5204 | 3292879.532 | 3210557.5437 | 3128235.5554 | 3045913.5671 | 2963591.5788 | 2881269.5905 | 2798947.6022 | 2716625.6139 | 2634303.6256 | 2551981.6373 | 2469659.649 | 2387337.6607 | 2305015.6724 | 2222693.6841 | 2140371.6958 | 2058049.7075 | 1975727.7192 | 1893405.7309 | 1811083.7426 | 1728761.7543 | 1646439.766 | 1564117.7777 | 1481795.7894 | 1399473.8011 | 1317151.8128 | 1234829.8245 | 1152507.8362 | 1070185.8479 | 987863.8596 | 905541.8713 | 823219.883 | 740897.8947 | 658575.9064 | 576253.9181 | 493931.9298 | 411609.9415 | 329287.9532 | 246965.9649 | 164643.9766 | 82321.9883 | 3.7253e-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation | [7 empty] | 154353.7281 | 297141.2168 | 274831.9579 | 254251.4609 | 235152.7596 | 217535.8541 | 201194.9394 | 186130.0155 | 183660.3559 | 183619.1949 | 183660.3559 | 183619.1949 | 183660.3559 | 183619.1949 | 183660.3559 | 183619.1949 | 183660.3559 | 183619.1949 | 183660.3559 | 183619.1949 | 91830.178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) | [7 empty] | 0 | -19963.5967 | -79500.7458 | -132854.8839 | -180505.1373 | -222862.1855 | -260336.7084 | -293282.3468 | -322052.7416 | -350138.6701 | -378213.191 | -406299.1195 | -434373.6403 | -462459.5689 | -490534.0897 | -518620.0183 | -546694.5391 | -574780.4677 | -602854.9885 | -630940.9171 | -659015.4379 | -661650.6327 | -638835.0936 | -616019.5546 | -593204.0155 | -570388.4764 | -547572.9374 | -524757.3983 | -501941.8593 | -479126.3202 | -456310.7812 | -433495.2421 | -410679.703 | -387864.164 | -365048.6249 | -342233.0859 | -319417.5468 | -296602.0077 | -273786.4687 | -250970.9296 | -228155.3906 | -205339.8515 | -182524.3125 | -159708.7734 | -136893.2343 | -114077.6953 | -91262.1562 | -68446.6172 | -45631.0781 | -22815.5391 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11
|  |  | ADIT (e.o.y.) | [7 empty] | -19963.5967 | -79500.7458 | -132854.8839 | -180505.1373 | -222862.1855 | -260336.7084 | -293282.3468 | -322052.7416 | -350138.6701 | -378213.191 | -406299.1195 | -434373.6403 | -462459.5689 | -490534.0897 | -518620.0183 | -546694.5391 | -574780.4677 | -602854.9885 | -630940.9171 | -659015.4379 | -661650.6327 | -638835.0936 | -616019.5546 | -593204.0155 | -570388.4764 | -547572.9374 | -524757.3983 | -501941.8593 | -479126.3202 | -456310.7812 | -433495.2421 | -410679.703 | -387864.164 | -365048.6249 | -342233.0859 | -319417.5468 | -296602.0077 | -273786.4687 | -250970.9296 | -228155.3906 | -205339.8515 | -182524.3125 | -159708.7734 | -136893.2343 | -114077.6953 | -91262.1562 | -68446.6172 | -45631.0781 | -22815.5391 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11
|  |  | Net Rate Base | [7 empty] | 4064956.6226 | 3942884.2613 | 3804116.6294 | 3671292.4454 | 3543966.8063 | 3421729.0324 | 3304196.9635 | 3191016.9586 | 3080266.8086 | 2969864.5956 | 2859462.3826 | 2749060.1697 | 2638657.9567 | 2528255.7437 | 2417853.5307 | 2307451.3177 | 2197049.1047 | 2086646.8917 | 1976244.6787 | 1865842.4657 | 1768165.6196 | 1695933.8034 | 1636427.3542 | 1576920.905 | 1517414.4557 | 1457908.0065 | 1398401.5572 | 1338895.108 | 1279388.6587 | 1219882.2095 | 1160375.7602 | 1100869.311 | 1041362.8618 | 981856.4125 | 922349.9633 | 862843.514 | 803337.0648 | 743830.6155 | 684324.1663 | 624817.7171 | 565311.2678 | 505804.8186 | 446298.3693 | 386791.9201 | 327285.4708 | 267779.0216 | 208272.5724 | 148766.1231 | 89259.6739 | 29753.2246 | 1.8335e-09 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11 | -2.9104e-11
|  |  | Pre-Tax return on rate base | [7 empty] | 363000.6264 | 352099.5645 | 339707.615 | 327846.4154 | 316476.2358 | 305560.4026 | 295064.7888 | 284957.8144 | 275067.826 | 265208.9084 | 255349.9908 | 245491.0731 | 235632.1555 | 225773.2379 | 215914.3203 | 206055.4027 | 196196.485 | 186337.5674 | 176478.6498 | 166619.7322 | 157897.1898 | 151446.8886 | 146132.9627 | 140819.0368 | 135505.1109 | 130191.185 | 124877.2591 | 119563.3331 | 114249.4072 | 108935.4813 | 103621.5554 | 98307.6295 | 92993.7036 | 87679.7776 | 82365.8517 | 77051.9258 | 71737.9999 | 66424.074 | 61110.1481 | 55796.2221 | 50482.2962 | 45168.3703 | 39854.4444 | 34540.5185 | 29226.5925 | 23912.6666 | 18598.7407 | 13284.8148 | 7970.8889 | 2656.963 | 1.6374e-10 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12 | -2.599e-12
|  | Investment year in service | [8 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93
|  | 2034 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
|  |  | Book depreciation | [8 empty] | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 84133.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service | [7 empty] | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 4206653.6022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation | [8 empty] | -84133.072 | -168266.1441 | -252399.2161 | -336532.2882 | -420665.3602 | -504798.4323 | -588931.5043 | -673064.5764 | -757197.6484 | -841330.7204 | -925463.7925 | -1009596.8645 | -1093729.9366 | -1177863.0086 | -1261996.0807 | -1346129.1527 | -1430262.2247 | -1514395.2968 | -1598528.3688 | -1682661.4409 | -1766794.5129 | -1850927.585 | -1935060.657 | -2019193.7291 | -2103326.8011 | -2187459.8731 | -2271592.9452 | -2355726.0172 | -2439859.0893 | -2523992.1613 | -2608125.2334 | -2692258.3054 | -2776391.3774 | -2860524.4495 | -2944657.5215 | -3028790.5936 | -3112923.6656 | -3197056.7377 | -3281189.8097 | -3365322.8818 | -3449455.9538 | -3533589.0258 | -3617722.0979 | -3701855.1699 | -3785988.242 | -3870121.314 | -3954254.3861 | -4038387.4581 | -4122520.5301 | -4206653.6022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) | [8 empty] | 4206653.6022 | 4122520.5301 | 4038387.4581 | 3954254.3861 | 3870121.314 | 3785988.242 | 3701855.1699 | 3617722.0979 | 3533589.0258 | 3449455.9538 | 3365322.8818 | 3281189.8097 | 3197056.7377 | 3112923.6656 | 3028790.5936 | 2944657.5215 | 2860524.4495 | 2776391.3774 | 2692258.3054 | 2608125.2334 | 2523992.1613 | 2439859.0893 | 2355726.0172 | 2271592.9452 | 2187459.8731 | 2103326.8011 | 2019193.7291 | 1935060.657 | 1850927.585 | 1766794.5129 | 1682661.4409 | 1598528.3688 | 1514395.2968 | 1430262.2247 | 1346129.1527 | 1261996.0807 | 1177863.0086 | 1093729.9366 | 1009596.8645 | 925463.7925 | 841330.7204 | 757197.6484 | 673064.5764 | 588931.5043 | 504798.4323 | 420665.3602 | 336532.2882 | 252399.2161 | 168266.1441 | 84133.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) | [7 empty] | 4206653.6022 | 4122520.5301 | 4038387.4581 | 3954254.3861 | 3870121.314 | 3785988.242 | 3701855.1699 | 3617722.0979 | 3533589.0258 | 3449455.9538 | 3365322.8818 | 3281189.8097 | 3197056.7377 | 3112923.6656 | 3028790.5936 | 2944657.5215 | 2860524.4495 | 2776391.3774 | 2692258.3054 | 2608125.2334 | 2523992.1613 | 2439859.0893 | 2355726.0172 | 2271592.9452 | 2187459.8731 | 2103326.8011 | 2019193.7291 | 1935060.657 | 1850927.585 | 1766794.5129 | 1682661.4409 | 1598528.3688 | 1514395.2968 | 1430262.2247 | 1346129.1527 | 1261996.0807 | 1177863.0086 | 1093729.9366 | 1009596.8645 | 925463.7925 | 841330.7204 | 757197.6484 | 673064.5764 | 588931.5043 | 504798.4323 | 420665.3602 | 336532.2882 | 252399.2161 | 168266.1441 | 84133.072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation | [8 empty] | 157749.5101 | 303678.3235 | 280878.261 | 259844.993 | 240326.1203 | 222321.6429 | 205621.2281 | 190224.8759 | 187700.8837 | 187658.8172 | 187700.8837 | 187658.8172 | 187700.8837 | 187658.8172 | 187700.8837 | 187658.8172 | 187700.8837 | 187658.8172 | 187700.8837 | 187658.8172 | 93850.4419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) | [8 empty] | 0 | -20402.7958 | -81249.7623 | -135777.6914 | -184476.2503 | -227765.1536 | -266064.116 | -299734.5584 | -329137.9019 | -357841.7209 | -386533.8812 | -415237.7002 | -443929.8604 | -472633.6794 | -501325.8397 | -530029.6587 | -558721.819 | -587425.638 | -616117.7983 | -644821.6173 | -673513.7775 | -676206.9466 | -652889.4657 | -629571.9848 | -606254.5038 | -582937.0229 | -559619.542 | -536302.0611 | -512984.5802 | -489667.0993 | -466349.6183 | -443032.1374 | -419714.6565 | -396397.1756 | -373079.6947 | -349762.2138 | -326444.7328 | -303127.2519 | -279809.771 | -256492.2901 | -233174.8092 | -209857.3283 | -186539.8473 | -163222.3664 | -139904.8855 | -116587.4046 | -93269.9237 | -69952.4428 | -46634.9618 | -23317.4809 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10
|  |  | ADIT (e.o.y.) | [8 empty] | -20402.7958 | -81249.7623 | -135777.6914 | -184476.2503 | -227765.1536 | -266064.116 | -299734.5584 | -329137.9019 | -357841.7209 | -386533.8812 | -415237.7002 | -443929.8604 | -472633.6794 | -501325.8397 | -530029.6587 | -558721.819 | -587425.638 | -616117.7983 | -644821.6173 | -673513.7775 | -676206.9466 | -652889.4657 | -629571.9848 | -606254.5038 | -582937.0229 | -559619.542 | -536302.0611 | -512984.5802 | -489667.0993 | -466349.6183 | -443032.1374 | -419714.6565 | -396397.1756 | -373079.6947 | -349762.2138 | -326444.7328 | -303127.2519 | -279809.771 | -256492.2901 | -233174.8092 | -209857.3283 | -186539.8473 | -163222.3664 | -139904.8855 | -116587.4046 | -93269.9237 | -69952.4428 | -46634.9618 | -23317.4809 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10
|  |  | Net Rate Base | [8 empty] | 4154385.6683 | 4029627.7151 | 3887807.1953 | 3752060.8792 | 3621934.0761 | 3497007.0712 | 3376889.2967 | 3261219.3317 | 3148032.6784 | 3035201.6167 | 2922370.5551 | 2809539.4934 | 2696708.4317 | 2583877.37 | 2471046.3083 | 2358215.2467 | 2245384.185 | 2132553.1233 | 2019722.0616 | 1906890.9999 | 1807065.2632 | 1733244.3471 | 1672428.756 | 1611613.1649 | 1550797.5737 | 1489981.9826 | 1429166.3915 | 1368350.8004 | 1307535.2092 | 1246719.6181 | 1185904.027 | 1125088.4358 | 1064272.8447 | 1003457.2536 | 942641.6625 | 881826.0713 | 821010.4802 | 760194.8891 | 699379.298 | 638563.7068 | 577748.1157 | 516932.5246 | 456116.9335 | 395301.3423 | 334485.7512 | 273670.1601 | 212854.5689 | 152038.9778 | 91223.3867 | 30407.7956 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10 | 1.4552e-10
|  |  | Pre-Tax return on rate base | [8 empty] | 370986.6402 | 359845.755 | 347181.1825 | 335059.0365 | 323438.713 | 312282.7315 | 301556.2142 | 291226.8863 | 281119.3182 | 271043.5044 | 260967.6906 | 250891.8768 | 240816.063 | 230740.2491 | 220664.4353 | 210588.6215 | 200512.8077 | 190436.9939 | 180361.1801 | 170285.3663 | 161370.928 | 154778.7202 | 149347.8879 | 143917.0556 | 138486.2233 | 133055.391 | 127624.5588 | 122193.7265 | 116762.8942 | 111332.0619 | 105901.2296 | 100470.3973 | 95039.565 | 89608.7327 | 84177.9005 | 78747.0682 | 73316.2359 | 67885.4036 | 62454.5713 | 57023.739 | 51592.9067 | 46162.0744 | 40731.2422 | 35300.4099 | 29869.5776 | 24438.7453 | 19007.913 | 13577.0807 | 8146.2484 | 2715.4161 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11 | 1.2995e-11
|  | Investment year in service | [9 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92
|  | 2035 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
|  |  | Book depreciation | [9 empty] | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 85983.9996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service | [8 empty] | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 4299199.9814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation | [9 empty] | -85983.9996 | -171967.9993 | -257951.9989 | -343935.9985 | -429919.9981 | -515903.9978 | -601887.9974 | -687871.997 | -773855.9967 | -859839.9963 | -945823.9959 | -1031807.9955 | -1117791.9952 | -1203775.9948 | -1289759.9944 | -1375743.9941 | -1461727.9937 | -1547711.9933 | -1633695.9929 | -1719679.9926 | -1805663.9922 | -1891647.9918 | -1977631.9915 | -2063615.9911 | -2149599.9907 | -2235583.9903 | -2321567.99 | -2407551.9896 | -2493535.9892 | -2579519.9889 | -2665503.9885 | -2751487.9881 | -2837471.9878 | -2923455.9874 | -3009439.987 | -3095423.9866 | -3181407.9863 | -3267391.9859 | -3353375.9855 | -3439359.9852 | -3525343.9848 | -3611327.9844 | -3697311.984 | -3783295.9837 | -3869279.9833 | -3955263.9829 | -4041247.9826 | -4127231.9822 | -4213215.9818 | -4299199.9814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) | [9 empty] | 4299199.9814 | 4213215.9818 | 4127231.9822 | 4041247.9826 | 3955263.9829 | 3869279.9833 | 3783295.9837 | 3697311.984 | 3611327.9844 | 3525343.9848 | 3439359.9852 | 3353375.9855 | 3267391.9859 | 3181407.9863 | 3095423.9866 | 3009439.987 | 2923455.9874 | 2837471.9878 | 2751487.9881 | 2665503.9885 | 2579519.9889 | 2493535.9892 | 2407551.9896 | 2321567.99 | 2235583.9903 | 2149599.9907 | 2063615.9911 | 1977631.9915 | 1891647.9918 | 1805663.9922 | 1719679.9926 | 1633695.9929 | 1547711.9933 | 1461727.9937 | 1375743.9941 | 1289759.9944 | 1203775.9948 | 1117791.9952 | 1031807.9955 | 945823.9959 | 859839.9963 | 773855.9967 | 687871.997 | 601887.9974 | 515903.9978 | 429919.9981 | 343935.9985 | 257951.9989 | 171967.9993 | 85983.9996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) | [8 empty] | 4299199.9814 | 4213215.9818 | 4127231.9822 | 4041247.9826 | 3955263.9829 | 3869279.9833 | 3783295.9837 | 3697311.984 | 3611327.9844 | 3525343.9848 | 3439359.9852 | 3353375.9855 | 3267391.9859 | 3181407.9863 | 3095423.9866 | 3009439.987 | 2923455.9874 | 2837471.9878 | 2751487.9881 | 2665503.9885 | 2579519.9889 | 2493535.9892 | 2407551.9896 | 2321567.99 | 2235583.9903 | 2149599.9907 | 2063615.9911 | 1977631.9915 | 1891647.9918 | 1805663.9922 | 1719679.9926 | 1633695.9929 | 1547711.9933 | 1461727.9937 | 1375743.9941 | 1289759.9944 | 1203775.9948 | 1117791.9952 | 1031807.9955 | 945823.9959 | 859839.9963 | 773855.9967 | 687871.997 | 601887.9974 | 515903.9978 | 429919.9981 | 343935.9985 | 257951.9989 | 171967.9993 | 85983.9996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation | [9 empty] | 161219.9993 | 310359.2467 | 287057.5828 | 265561.5829 | 245613.2949 | 227212.719 | 210144.8951 | 194409.8232 | 191830.3032 | 191787.3112 | 191830.3032 | 191787.3112 | 191830.3032 | 191787.3112 | 191830.3032 | 191787.3112 | 191830.3032 | 191787.3112 | 191830.3032 | 191787.3112 | 95915.1516 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) | [9 empty] | 0 | -20851.6573 | -83037.257 | -138764.8006 | -188534.7278 | -232775.987 | -271917.5266 | -306328.7187 | -336378.9357 | -365714.2388 | -395037.6265 | -424372.9296 | -453696.3174 | -483031.6204 | -512355.0082 | -541690.3112 | -571013.699 | -600349.002 | -629672.3898 | -659007.6929 | -688331.0807 | -691083.4994 | -667253.0339 | -643422.5684 | -619592.1029 | -595761.6374 | -571931.1719 | -548100.7064 | -524270.2409 | -500439.7754 | -476609.3099 | -452778.8444 | -428948.3789 | -405117.9135 | -381287.448 | -357456.9825 | -333626.517 | -309796.0515 | -285965.586 | -262135.1205 | -238304.655 | -214474.1895 | -190643.724 | -166813.2585 | -142982.793 | -119152.3275 | -95321.862 | -71491.3965 | -47660.931 | -23830.4655 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10
|  |  | ADIT (e.o.y.) | [9 empty] | -20851.6573 | -83037.257 | -138764.8006 | -188534.7278 | -232775.987 | -271917.5266 | -306328.7187 | -336378.9357 | -365714.2388 | -395037.6265 | -424372.9296 | -453696.3174 | -483031.6204 | -512355.0082 | -541690.3112 | -571013.699 | -600349.002 | -629672.3898 | -659007.6929 | -688331.0807 | -691083.4994 | -667253.0339 | -643422.5684 | -619592.1029 | -595761.6374 | -571931.1719 | -548100.7064 | -524270.2409 | -500439.7754 | -476609.3099 | -452778.8444 | -428948.3789 | -405117.9135 | -381287.448 | -357456.9825 | -333626.517 | -309796.0515 | -285965.586 | -262135.1205 | -238304.655 | -214474.1895 | -190643.724 | -166813.2585 | -142982.793 | -119152.3275 | -95321.862 | -71491.3965 | -47660.931 | -23830.4655 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10
|  |  | Net Rate Base | [9 empty] | 4245782.153 | 4118279.5248 | 3973338.9536 | 3834606.2186 | 3701616.6257 | 3573941.2267 | 3451180.8612 | 3332966.157 | 3217289.3974 | 3101976.0523 | 2986662.7073 | 2871349.3622 | 2756036.0172 | 2640722.6722 | 2525409.3271 | 2410095.9821 | 2294782.637 | 2179469.292 | 2064155.947 | 1948842.6019 | 1846820.699 | 1771375.7228 | 1709222.1886 | 1647068.6545 | 1584915.1204 | 1522761.5862 | 1460608.0521 | 1398454.518 | 1336300.9838 | 1274147.4497 | 1211993.9156 | 1149840.3814 | 1087686.8473 | 1025533.3132 | 963379.779 | 901226.2449 | 839072.7108 | 776919.1766 | 714765.6425 | 652612.1084 | 590458.5743 | 528305.0401 | 466151.506 | 403997.9719 | 341844.4377 | 279690.9036 | 217537.3695 | 155383.8353 | 93230.3012 | 31076.7671 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10
|  |  | Pre-Tax return on rate base | [9 empty] | 379148.3463 | 367762.3616 | 354819.1686 | 342430.3353 | 330554.3647 | 319152.9515 | 308190.4509 | 297633.8778 | 287303.9432 | 277006.4615 | 266708.9798 | 256411.498 | 246114.0163 | 235816.5346 | 225519.0529 | 215221.5712 | 204924.0895 | 194626.6078 | 184329.1261 | 174031.6444 | 164921.0884 | 158183.852 | 152633.5414 | 147083.2308 | 141532.9202 | 135982.6097 | 130432.2991 | 124881.9885 | 119331.6779 | 113781.3673 | 108231.0567 | 102680.7461 | 97130.4355 | 91580.1249 | 86029.8143 | 80479.5037 | 74929.1931 | 69378.8825 | 63828.5719 | 58278.2613 | 52727.9507 | 47177.6401 | 41627.3295 | 36077.0189 | 30526.7083 | 24976.3977 | 19426.0871 | 13875.7765 | 8325.4659 | 2775.1553 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11
|  | Investment year in service | [10 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91
|  | 2036 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
|  |  | Book depreciation | [10 empty] | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 87875.6476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service | [9 empty] | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 4393782.381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation | [10 empty] | -87875.6476 | -175751.2952 | -263626.9429 | -351502.5905 | -439378.2381 | -527253.8857 | -615129.5333 | -703005.181 | -790880.8286 | -878756.4762 | -966632.1238 | -1054507.7714 | -1142383.4191 | -1230259.0667 | -1318134.7143 | -1406010.3619 | -1493886.0096 | -1581761.6572 | -1669637.3048 | -1757512.9524 | -1845388.6 | -1933264.2477 | -2021139.8953 | -2109015.5429 | -2196891.1905 | -2284766.8381 | -2372642.4858 | -2460518.1334 | -2548393.781 | -2636269.4286 | -2724145.0762 | -2812020.7239 | -2899896.3715 | -2987772.0191 | -3075647.6667 | -3163523.3143 | -3251398.962 | -3339274.6096 | -3427150.2572 | -3515025.9048 | -3602901.5524 | -3690777.2001 | -3778652.8477 | -3866528.4953 | -3954404.1429 | -4042279.7906 | -4130155.4382 | -4218031.0858 | -4305906.7334 | -4393782.381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) | [10 empty] | 4393782.381 | 4305906.7334 | 4218031.0858 | 4130155.4382 | 4042279.7906 | 3954404.1429 | 3866528.4953 | 3778652.8477 | 3690777.2001 | 3602901.5524 | 3515025.9048 | 3427150.2572 | 3339274.6096 | 3251398.962 | 3163523.3143 | 3075647.6667 | 2987772.0191 | 2899896.3715 | 2812020.7239 | 2724145.0762 | 2636269.4286 | 2548393.781 | 2460518.1334 | 2372642.4858 | 2284766.8381 | 2196891.1905 | 2109015.5429 | 2021139.8953 | 1933264.2477 | 1845388.6 | 1757512.9524 | 1669637.3048 | 1581761.6572 | 1493886.0096 | 1406010.3619 | 1318134.7143 | 1230259.0667 | 1142383.4191 | 1054507.7714 | 966632.1238 | 878756.4762 | 790880.8286 | 703005.181 | 615129.5333 | 527253.8857 | 439378.2381 | 351502.5905 | 263626.9429 | 175751.2952 | 87875.6476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) | [9 empty] | 4393782.381 | 4305906.7334 | 4218031.0858 | 4130155.4382 | 4042279.7906 | 3954404.1429 | 3866528.4953 | 3778652.8477 | 3690777.2001 | 3602901.5524 | 3515025.9048 | 3427150.2572 | 3339274.6096 | 3251398.962 | 3163523.3143 | 3075647.6667 | 2987772.0191 | 2899896.3715 | 2812020.7239 | 2724145.0762 | 2636269.4286 | 2548393.781 | 2460518.1334 | 2372642.4858 | 2284766.8381 | 2196891.1905 | 2109015.5429 | 2021139.8953 | 1933264.2477 | 1845388.6 | 1757512.9524 | 1669637.3048 | 1581761.6572 | 1493886.0096 | 1406010.3619 | 1318134.7143 | 1230259.0667 | 1142383.4191 | 1054507.7714 | 966632.1238 | 878756.4762 | 790880.8286 | 703005.181 | 615129.5333 | 527253.8857 | 439378.2381 | 351502.5905 | 263626.9429 | 175751.2952 | 87875.6476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation | [10 empty] | 164766.8393 | 317187.1501 | 293372.8496 | 271403.9377 | 251016.7874 | 232211.3988 | 214768.0828 | 198686.8393 | 196050.5698 | 196006.632 | 196050.5698 | 196006.632 | 196050.5698 | 196006.632 | 196050.5698 | 196006.632 | 196050.5698 | 196006.632 | 196050.5698 | 196006.632 | 98025.2849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) | [10 empty] | 0 | -21310.3938 | -84864.0767 | -141817.6262 | -192682.4918 | -237897.0587 | -277899.7121 | -313067.9505 | -343779.2723 | -373759.952 | -403728.4543 | -433709.134 | -463677.6363 | -493658.316 | -523626.8184 | -553607.4981 | -583576.0004 | -613556.6801 | -643525.1824 | -673505.8621 | -703474.3644 | -706287.3364 | -681932.6007 | -657577.8649 | -633223.1292 | -608868.3935 | -584513.6577 | -560158.922 | -535804.1862 | -511449.4505 | -487094.7148 | -462739.979 | -438385.2433 | -414030.5075 | -389675.7718 | -365321.0361 | -340966.3003 | -316611.5646 | -292256.8289 | -267902.0931 | -243547.3574 | -219192.6216 | -194837.8859 | -170483.1502 | -146128.4144 | -121773.6787 | -97418.943 | -73064.2072 | -48709.4715 | -24354.7357 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10
|  |  | ADIT (e.o.y.) | [10 empty] | -21310.3938 | -84864.0767 | -141817.6262 | -192682.4918 | -237897.0587 | -277899.7121 | -313067.9505 | -343779.2723 | -373759.952 | -403728.4543 | -433709.134 | -463677.6363 | -493658.316 | -523626.8184 | -553607.4981 | -583576.0004 | -613556.6801 | -643525.1824 | -673505.8621 | -703474.3644 | -706287.3364 | -681932.6007 | -657577.8649 | -633223.1292 | -608868.3935 | -584513.6577 | -560158.922 | -535804.1862 | -511449.4505 | -487094.7148 | -462739.979 | -438385.2433 | -414030.5075 | -389675.7718 | -365321.0361 | -340966.3003 | -316611.5646 | -292256.8289 | -267902.0931 | -243547.3574 | -219192.6216 | -194837.8859 | -170483.1502 | -146128.4144 | -121773.6787 | -97418.943 | -73064.2072 | -48709.4715 | -24354.7357 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10
|  |  | Net Rate Base | [10 empty] | 4339189.3603 | 4208881.6744 | 4060752.4105 | 3918967.5554 | 3783052.1915 | 3652567.9337 | 3527106.8402 | 3406291.4124 | 3288069.7641 | 3170219.5255 | 3052369.2868 | 2934519.0482 | 2816668.8096 | 2698818.5709 | 2580968.3323 | 2463118.0937 | 2345267.8551 | 2227417.6164 | 2109567.3778 | 1991717.1392 | 1887450.7544 | 1810345.9887 | 1746825.0768 | 1683304.1649 | 1619783.253 | 1556262.3411 | 1492741.4292 | 1429220.5174 | 1365699.6055 | 1302178.6936 | 1238657.7817 | 1175136.8698 | 1111615.9579 | 1048095.0461 | 984574.1342 | 921053.2223 | 857532.3104 | 794011.3985 | 730490.4866 | 666969.5748 | 603448.6629 | 539927.751 | 476406.8391 | 412885.9272 | 349365.0154 | 285844.1035 | 222323.1916 | 158802.2797 | 95281.3678 | 31760.4559 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10 | -3.5652e-10
|  |  | Pre-Tax return on rate base | [10 empty] | 387489.6099 | 375853.1335 | 362625.1903 | 349963.8027 | 337826.5607 | 326174.3165 | 314970.6408 | 304181.8231 | 293624.6299 | 283100.6036 | 272576.5773 | 262052.551 | 251528.5247 | 241004.4984 | 230480.4721 | 219956.4458 | 209432.4195 | 198908.3931 | 188384.3668 | 177860.3405 | 168549.3524 | 161663.8968 | 155991.4794 | 150319.0619 | 144646.6445 | 138974.2271 | 133301.8096 | 127629.3922 | 121956.9748 | 116284.5573 | 110612.1399 | 104939.7225 | 99267.305 | 93594.8876 | 87922.4702 | 82250.0528 | 76577.6353 | 70905.2179 | 65232.8005 | 59560.383 | 53887.9656 | 48215.5482 | 42543.1307 | 36870.7133 | 31198.2959 | 25525.8784 | 19853.461 | 14181.0436 | 8508.6261 | 2836.2087 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11 | -3.1837e-11
|  |  | Total CAPEX cost rollup |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100
|  |  | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
|  |  | Book depreciation | 0 | 72245.446 | 146080.2918 | 221539.5042 | 298658.8193 | 377474.7594 | 458024.6501 | 540346.6384 | 624479.7104 | 710463.71 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 798339.3577 | 726093.9117 | 652259.0658 | 576799.8534 | 499680.5383 | 420864.5983 | 340314.7076 | 257992.7193 | 173859.6472 | 87875.6476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service | 3612272.3 | 3612272.3 | 7304014.5906 | 11076975.2116 | 14932940.9662 | 18873737.9675 | 22901232.5028 | 27017331.9179 | 31223985.52 | 31223985.52 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 39916967.8825 | 36304695.5825 | 32612953.2919 | 28839992.6709 | 24984026.9163 | 21043229.915 | 17015735.3797 | 12899635.9647 | 8692982.3625 | 4393782.381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation | 0 | -72245.446 | -218325.7378 | -439865.242 | -738524.0614 | -1115998.8207 | -1574023.4708 | -2114370.1091 | -2738849.8195 | -3449313.5296 | -4247652.8872 | -5045992.2449 | -5844331.6025 | -6642670.9602 | -7441010.3178 | -8239349.6755 | -9037689.0331 | -9836028.3908 | -10634367.7484 | -11432707.1061 | -12231046.4637 | -13029385.8214 | -13827725.179 | -14626064.5367 | -15424403.8943 | -16222743.252 | -17021082.6096 | -17819421.9673 | -18617761.3249 | -19416100.6826 | -20214440.0402 | -21012779.3979 | -21811118.7555 | -22609458.1132 | -23407797.4708 | -24206136.8285 | -25004476.1861 | -25802815.5438 | -26601154.9014 | -27399494.2591 | -28197833.6167 | -28996172.9744 | -29794512.332 | -30592851.6897 | -31391191.0473 | -32189530.405 | -32987869.7626 | -33786209.1203 | -34584548.4779 | -35382887.8356 | -36181227.1932 | -33295048.8049 | -30255565.5801 | -27059404.8125 | -23703119.5962 | -20183187.1933 | -16496007.3656 | -12637900.6698 | -8605106.7149 | -4393782.381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) | 0 | 3612272.3 | 7231769.1446 | 10858649.4738 | 14493075.7242 | 18135213.9061 | 21785233.6821 | 25443308.4471 | 29109615.4109 | 32784335.682 | 36467654.353 | 35669314.9953 | 34870975.6377 | 34072636.28 | 33274296.9224 | 32475957.5647 | 31677618.2071 | 30879278.8494 | 30080939.4918 | 29282600.1341 | 28484260.7765 | 27685921.4188 | 26887582.0612 | 26089242.7035 | 25290903.3459 | 24492563.9882 | 23694224.6306 | 22895885.2729 | 22097545.9152 | 21299206.5576 | 20500867.1999 | 19702527.8423 | 18904188.4846 | 18105849.127 | 17307509.7693 | 16509170.4117 | 15710831.054 | 14912491.6964 | 14114152.3387 | 13315812.9811 | 12517473.6234 | 11719134.2658 | 10920794.9081 | 10122455.5505 | 9324116.1928 | 8525776.8352 | 7727437.4775 | 6929098.1199 | 6130758.7622 | 5332419.4046 | 4534080.0469 | 3735740.6893 | 3009646.7776 | 2357387.7118 | 1780587.8584 | 1280907.3201 | 860042.7218 | 519728.0142 | 261735.2949 | 87875.6476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) | 3612272.3 | 7231769.1446 | 10858649.4738 | 14493075.7242 | 18135213.9061 | 21785233.6821 | 25443308.4471 | 29109615.4109 | 32784335.682 | 36467654.353 | 35669314.9953 | 34870975.6377 | 34072636.28 | 33274296.9224 | 32475957.5647 | 31677618.2071 | 30879278.8494 | 30080939.4918 | 29282600.1341 | 28484260.7765 | 27685921.4188 | 26887582.0612 | 26089242.7035 | 25290903.3459 | 24492563.9882 | 23694224.6306 | 22895885.2729 | 22097545.9152 | 21299206.5576 | 20500867.1999 | 19702527.8423 | 18904188.4846 | 18105849.127 | 17307509.7693 | 16509170.4117 | 15710831.054 | 14912491.6964 | 14114152.3387 | 13315812.9811 | 12517473.6234 | 11719134.2658 | 10920794.9081 | 10122455.5505 | 9324116.1928 | 8525776.8352 | 7727437.4775 | 6929098.1199 | 6130758.7622 | 5332419.4046 | 4534080.0469 | 3735740.6893 | 3009646.7776 | 2357387.7118 | 1780587.8584 | 1280907.3201 | 860042.7218 | 519728.0142 | 261735.2949 | 87875.6476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation | 0 | 135460.2112 | 399210.2732 | 649184.3207 | 886596.4357 | 1112470.6738 | 1327853.6197 | 1533634.2694 | 1730721.1767 | 1929976.6326 | 2133579.5858 | 2173306.217 | 2058097.1537 | 1964727.8288 | 1891720.484 | 1837978.768 | 1802237.7186 | 1783573.5578 | 1780897.6936 | 1780893.3505 | 1780897.6936 | 1700303.5555 | 1537391.4558 | 1370850.3855 | 1200690.316 | 1026741.8206 | 849011.3627 | 667325.9303 | 481688.3229 | 291921.7836 | 98025.2849 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) | 0 | 0 | -17519.9722 | -87674.9465 | -206196.7074 | -369143.6178 | -572847.7355 | -813920.8345 | -1089210.5014 | -1395805.3238 | -1733793.3303 | -2103855.1595 | -2484927.2246 | -2834069.0977 | -3157333.6625 | -3460364.2417 | -3748500.3043 | -4026730.735 | -4299788.3936 | -4572104.4364 | -4844419.2755 | -5116735.3183 | -5366714.6958 | -5571542.9848 | -5730214.4161 | -5841725.9842 | -5905027.7269 | -5919071.4731 | -5882761.1017 | -5795001.2674 | -5654647.6367 | -5460555.5915 | -5239295.8385 | -5018036.0855 | -4796776.3326 | -4575516.5796 | -4354256.8266 | -4132997.0737 | -3911737.3207 | -3690477.5677 | -3469217.8147 | -3247958.0618 | -3026698.3088 | -2805438.5558 | -2584178.8028 | -2362919.0499 | -2141659.2969 | -1920399.5439 | -1699139.791 | -1477880.038 | -1256620.285 | -1035360.532 | -834123.6044 | -653350.0043 | -493489.925 | -355003.4638 | -238360.8403 | -144042.6191 | -72539.937 | -24354.7357 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10
|  |  | ADIT (e.o.y.) | 0 | -17519.9722 | -87674.9465 | -206196.7074 | -369143.6178 | -572847.7355 | -813920.8345 | -1089210.5014 | -1395805.3238 | -1733793.3303 | -2103855.1595 | -2484927.2246 | -2834069.0977 | -3157333.6625 | -3460364.2417 | -3748500.3043 | -4026730.735 | -4299788.3936 | -4572104.4364 | -4844419.2755 | -5116735.3183 | -5366714.6958 | -5571542.9848 | -5730214.4161 | -5841725.9842 | -5905027.7269 | -5919071.4731 | -5882761.1017 | -5795001.2674 | -5654647.6367 | -5460555.5915 | -5239295.8385 | -5018036.0855 | -4796776.3326 | -4575516.5796 | -4354256.8266 | -4132997.0737 | -3911737.3207 | -3690477.5677 | -3469217.8147 | -3247958.0618 | -3026698.3088 | -2805438.5558 | -2584178.8028 | -2362919.0499 | -2141659.2969 | -1920399.5439 | -1699139.791 | -1477880.038 | -1256620.285 | -1035360.532 | -834123.6044 | -653350.0043 | -493489.925 | -355003.4638 | -238360.8403 | -144042.6191 | -72539.937 | -24354.7357 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10
|  |  | Net Rate Base | 0 | 3567389.5909 | 7106131.5393 | 10600943.8947 | 14056076.1519 | 17475480.8498 | 20862837.0721 | 24221569.46 | 27554867.6431 | 30864304.4999 | 34149660.4292 | 32975754.1244 | 31812307.7977 | 30677765.221 | 29566278.2914 | 28472355.6129 | 27390833.0086 | 26316849.6063 | 25245823.3979 | 24175168.5993 | 23104513.8007 | 22045026.7329 | 21019283.5421 | 20039194.3242 | 19105763.4668 | 18220017.4538 | 17383005.3518 | 16595799.3067 | 15859495.0519 | 15175212.4267 | 14544095.907 | 13953432.4485 | 13376352.8438 | 12799273.2391 | 12222193.6344 | 11645114.0298 | 11068034.4251 | 10490954.8204 | 9913875.2157 | 9336795.611 | 8759716.0064 | 8182636.4017 | 7605556.797 | 7028477.1923 | 6451397.5877 | 5874317.983 | 5297238.3783 | 4720158.7736 | 4143079.1689 | 3565999.5643 | 2988919.9596 | 2437951.6652 | 1939780.4403 | 1495567.8205 | 1106500.8949 | 773792.8689 | 498683.6382 | 282440.3765 | 126358.1349 | 31760.4559 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10 | 9.1677e-10
|  |  | Pre-Tax return on rate base | 0 | 318567.8905 | 634577.5465 | 946664.2898 | 1255207.6004 | 1560560.4399 | 1863051.3505 | 2162986.1528 | 2460649.6805 | 2756182.3918 | 3049564.6763 | 2944734.8433 | 2840839.0863 | 2739524.4342 | 2640268.6514 | 2542581.3562 | 2446001.3877 | 2350094.6698 | 2254452.0294 | 2158842.5559 | 2063233.0824 | 1968620.8873 | 1877022.0203 | 1789500.0532 | 1706144.6776 | 1627047.5586 | 1552302.3779 | 1482004.8781 | 1416252.9081 | 1355146.4697 | 1298787.7645 | 1246041.5176 | 1194508.309 | 1142975.1003 | 1091441.8916 | 1039908.6829 | 988375.4742 | 936842.2655 | 885309.0568 | 833775.8481 | 782242.6394 | 730709.4307 | 679176.222 | 627643.0133 | 576109.8046 | 524576.5959 | 473043.3872 | 421510.1785 | 369976.9698 | 318443.7611 | 266910.5524 | 217709.0837 | 173222.3933 | 133554.2064 | 98810.5299 | 69099.7032 | 44532.4489 | 25221.9256 | 11283.7814 | 2836.2087 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11 | 8.1868e-11

## Rev Req't_Baseline_UG1PH
Assumptions | Value
Equipment Life flag | 56 |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Book life flag | 50 |  |  | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037
MACRS flag | 20 |  | Unescalated Baseline Costs (from Construction, with Overheads) |  | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2
|  |  | Miles unescalated |  | 4.96 | 4.96 | 4.96 | 4.96 | 4.96 | 4.96 | 4.96 | 4.96 | 4.96 | 4.96
|  |  | Cost per mile unescalated |  | 601670.6048 | 601670.6048 | 601670.6048 | 601670.6048 | 601670.6048 | 601670.6048 | 601670.6048 | 601670.6048 | 601670.6048 | 601670.6048
|  |  | CPI |  | 1 | 1.022 | 1.0445 | 1.0675 | 1.0909 | 1.1149 | 1.1395 | 1.1645 | 1.1902 | 1.2163
|  |  | Escalated with CPI |  | 2984286.2 | 3049940.4964 | 3117039.1873 | 3185614.0494 | 3255697.5585 | 3327322.9048 | 3400524.0087 | 3475335.5369 | 3551792.9187 | 3629932.3629
|  |  | Cost per mile escalated |  | 601670.6048 | 614907.3581 | 628435.32 | 642260.8971 | 656390.6368 | 670831.2308 | 685589.5179 | 700672.4873 | 716087.282 | 731841.2022
|  | Investment year in service |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100
QAQC check |  | 2027 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
2984286.2 |  |  | Book depreciation |  | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 59685.724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 2984286.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation |  | -59685.724 | -119371.448 | -179057.172 | -238742.896 | -298428.62 | -358114.344 | -417800.068 | -477485.792 | -537171.516 | -596857.24 | -656542.964 | -716228.688 | -775914.412 | -835600.136 | -895285.86 | -954971.584 | -1014657.308 | -1074343.032 | -1134028.756 | -1193714.48 | -1253400.204 | -1313085.928 | -1372771.652 | -1432457.376 | -1492143.1 | -1551828.824 | -1611514.548 | -1671200.272 | -1730885.996 | -1790571.72 | -1850257.444 | -1909943.168 | -1969628.892 | -2029314.616 | -2089000.34 | -2148686.064 | -2208371.788 | -2268057.512 | -2327743.236 | -2387428.96 | -2447114.684 | -2506800.408 | -2566486.132 | -2626171.856 | -2685857.58 | -2745543.304 | -2805229.028 | -2864914.752 | -2924600.476 | -2984286.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) |  | 2984286.2 | 2924600.476 | 2864914.752 | 2805229.028 | 2745543.304 | 2685857.58 | 2626171.856 | 2566486.132 | 2506800.408 | 2447114.684 | 2387428.96 | 2327743.236 | 2268057.512 | 2208371.788 | 2148686.064 | 2089000.34 | 2029314.616 | 1969628.892 | 1909943.168 | 1850257.444 | 1790571.72 | 1730885.996 | 1671200.272 | 1611514.548 | 1551828.824 | 1492143.1 | 1432457.376 | 1372771.652 | 1313085.928 | 1253400.204 | 1193714.48 | 1134028.756 | 1074343.032 | 1014657.308 | 954971.584 | 895285.86 | 835600.136 | 775914.412 | 716228.688 | 656542.964 | 596857.24 | 537171.516 | 477485.792 | 417800.068 | 358114.344 | 298428.62 | 238742.896 | 179057.172 | 119371.448 | 59685.724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) | 2984286.2 | 2924600.476 | 2864914.752 | 2805229.028 | 2745543.304 | 2685857.58 | 2626171.856 | 2566486.132 | 2506800.408 | 2447114.684 | 2387428.96 | 2327743.236 | 2268057.512 | 2208371.788 | 2148686.064 | 2089000.34 | 2029314.616 | 1969628.892 | 1909943.168 | 1850257.444 | 1790571.72 | 1730885.996 | 1671200.272 | 1611514.548 | 1551828.824 | 1492143.1 | 1432457.376 | 1372771.652 | 1313085.928 | 1253400.204 | 1193714.48 | 1134028.756 | 1074343.032 | 1014657.308 | 954971.584 | 895285.86 | 835600.136 | 775914.412 | 716228.688 | 656542.964 | 596857.24 | 537171.516 | 477485.792 | 417800.068 | 358114.344 | 298428.62 | 238742.896 | 179057.172 | 119371.448 | 59685.724 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation |  | 111910.7325 | 215435.6208 | 199260.7896 | 184339.3586 | 170492.2706 | 157719.5257 | 145871.9095 | 134949.422 | 133158.8502 | 133129.0074 | 133158.8502 | 133129.0074 | 133158.8502 | 133129.0074 | 133158.8502 | 133129.0074 | 133158.8502 | 133129.0074 | 133158.8502 | 133129.0074 | 66579.4251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) |  | 0 | -14474.1611 | -57640.245 | -96323.4744 | -130871.2292 | -161581.2636 | -188751.3318 | -212637.8331 | -233497.167 | -253860.2439 | -274215.0499 | -294578.1268 | -314932.9328 | -335296.0098 | -355650.8157 | -376013.8927 | -396368.6987 | -416731.7756 | -437086.5816 | -457449.6585 | -477804.4645 | -479715.0538 | -463173.1554 | -446631.257 | -430089.3586 | -413547.4602 | -397005.5618 | -380463.6634 | -363921.7649 | -347379.8665 | -330837.9681 | -314296.0697 | -297754.1713 | -281212.2729 | -264670.3745 | -248128.4761 | -231586.5777 | -215044.6793 | -198502.7809 | -181960.8825 | -165418.9841 | -148877.0857 | -132335.1873 | -115793.2888 | -99251.3904 | -82709.492 | -66167.5936 | -49625.6952 | -33083.7968 | -16541.8984 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10
|  |  | ADIT (e.o.y.) |  | -14474.1611 | -57640.245 | -96323.4744 | -130871.2292 | -161581.2636 | -188751.3318 | -212637.8331 | -233497.167 | -253860.2439 | -274215.0499 | -294578.1268 | -314932.9328 | -335296.0098 | -355650.8157 | -376013.8927 | -396368.6987 | -416731.7756 | -437086.5816 | -457449.6585 | -477804.4645 | -479715.0538 | -463173.1554 | -446631.257 | -430089.3586 | -413547.4602 | -397005.5618 | -380463.6634 | -363921.7649 | -347379.8665 | -330837.9681 | -314296.0697 | -297754.1713 | -281212.2729 | -264670.3745 | -248128.4761 | -231586.5777 | -215044.6793 | -198502.7809 | -181960.8825 | -165418.9841 | -148877.0857 | -132335.1873 | -115793.2888 | -99251.3904 | -82709.492 | -66167.5936 | -49625.6952 | -33083.7968 | -16541.8984 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10
|  |  | Net Rate Base |  | 2947206.2574 | 2858700.4109 | 2758090.0303 | 2661788.8142 | 2569474.1956 | 2480848.4203 | 2395634.4116 | 2313575.77 | 2233278.8406 | 2153234.1751 | 2073189.5096 | 1993144.8442 | 1913100.1787 | 1833055.5133 | 1753010.8478 | 1672966.1823 | 1592921.5169 | 1512876.8514 | 1432832.1859 | 1352787.5205 | 1281969.0988 | 1229599.0294 | 1186455.2038 | 1143311.3782 | 1100167.5526 | 1057023.727 | 1013879.9014 | 970736.0759 | 927592.2503 | 884448.4247 | 841304.5991 | 798160.7735 | 755016.9479 | 711873.1223 | 668729.2967 | 625585.4711 | 582441.6455 | 539297.8199 | 496153.9943 | 453010.1687 | 409866.3431 | 366722.5175 | 323578.692 | 280434.8664 | 237291.0408 | 194147.2152 | 151003.3896 | 107859.564 | 64715.7384 | 21571.9128 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10 | -2.8376e-10
|  |  | Pre-Tax return on rate base |  | 263185.5188 | 255281.9467 | 246297.4397 | 237697.7411 | 229454.0457 | 221539.7639 | 213930.153 | 206602.3163 | 199431.8005 | 192283.8118 | 185135.8232 | 177987.8346 | 170839.846 | 163691.8573 | 156543.8687 | 149395.8801 | 142247.8915 | 135099.9028 | 127951.9142 | 120803.9256 | 114479.8405 | 109803.1933 | 105950.4497 | 102097.7061 | 98244.9625 | 94392.2188 | 90539.4752 | 86686.7316 | 82833.9879 | 78981.2443 | 75128.5007 | 71275.7571 | 67423.0134 | 63570.2698 | 59717.5262 | 55864.7826 | 52012.0389 | 48159.2953 | 44306.5517 | 40453.8081 | 36601.0644 | 32748.3208 | 28895.5772 | 25042.8336 | 21190.0899 | 17337.3463 | 13484.6027 | 9631.8591 | 5779.1154 | 1926.3718 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11 | -2.534e-11
|  | Investment year in service |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99
QAQC check |  | 2028 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
3049940.4964 |  |  | Book depreciation |  |  | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 60998.8099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service |  | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 3049940.4964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation |  |  | -60998.8099 | -121997.6199 | -182996.4298 | -243995.2397 | -304994.0496 | -365992.8596 | -426991.6695 | -487990.4794 | -548989.2894 | -609988.0993 | -670986.9092 | -731985.7191 | -792984.5291 | -853983.339 | -914982.1489 | -975980.9588 | -1036979.7688 | -1097978.5787 | -1158977.3886 | -1219976.1986 | -1280975.0085 | -1341973.8184 | -1402972.6283 | -1463971.4383 | -1524970.2482 | -1585969.0581 | -1646967.8681 | -1707966.678 | -1768965.4879 | -1829964.2978 | -1890963.1078 | -1951961.9177 | -2012960.7276 | -2073959.5376 | -2134958.3475 | -2195957.1574 | -2256955.9673 | -2317954.7773 | -2378953.5872 | -2439952.3971 | -2500951.207 | -2561950.017 | -2622948.8269 | -2683947.6368 | -2744946.4468 | -2805945.2567 | -2866944.0666 | -2927942.8765 | -2988941.6865 | -3049940.4964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) |  |  | 3049940.4964 | 2988941.6865 | 2927942.8765 | 2866944.0666 | 2805945.2567 | 2744946.4468 | 2683947.6368 | 2622948.8269 | 2561950.017 | 2500951.207 | 2439952.3971 | 2378953.5872 | 2317954.7773 | 2256955.9673 | 2195957.1574 | 2134958.3475 | 2073959.5376 | 2012960.7276 | 1951961.9177 | 1890963.1078 | 1829964.2978 | 1768965.4879 | 1707966.678 | 1646967.8681 | 1585969.0581 | 1524970.2482 | 1463971.4383 | 1402972.6283 | 1341973.8184 | 1280975.0085 | 1219976.1986 | 1158977.3886 | 1097978.5787 | 1036979.7688 | 975980.9588 | 914982.1489 | 853983.339 | 792984.5291 | 731985.7191 | 670986.9092 | 609988.0993 | 548989.2894 | 487990.4794 | 426991.6695 | 365992.8596 | 304994.0496 | 243995.2397 | 182996.4298 | 121997.6199 | 60998.8099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) |  | 3049940.4964 | 2988941.6865 | 2927942.8765 | 2866944.0666 | 2805945.2567 | 2744946.4468 | 2683947.6368 | 2622948.8269 | 2561950.017 | 2500951.207 | 2439952.3971 | 2378953.5872 | 2317954.7773 | 2256955.9673 | 2195957.1574 | 2134958.3475 | 2073959.5376 | 2012960.7276 | 1951961.9177 | 1890963.1078 | 1829964.2978 | 1768965.4879 | 1707966.678 | 1646967.8681 | 1585969.0581 | 1524970.2482 | 1463971.4383 | 1402972.6283 | 1341973.8184 | 1280975.0085 | 1219976.1986 | 1158977.3886 | 1097978.5787 | 1036979.7688 | 975980.9588 | 914982.1489 | 853983.339 | 792984.5291 | 731985.7191 | 670986.9092 | 609988.0993 | 548989.2894 | 487990.4794 | 426991.6695 | 365992.8596 | 304994.0496 | 243995.2397 | 182996.4298 | 121997.6199 | 60998.8099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation |  |  | 114372.7686 | 220175.2044 | 203644.5269 | 188394.8245 | 174243.1006 | 161189.3552 | 149081.0915 | 137918.3092 | 136088.3449 | 136057.8455 | 136088.3449 | 136057.8455 | 136088.3449 | 136057.8455 | 136088.3449 | 136057.8455 | 136088.3449 | 136057.8455 | 136088.3449 | 136057.8455 | 68044.1725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) |  |  | 0 | -14792.5927 | -58908.3304 | -98442.5909 | -133750.3963 | -165136.0514 | -192903.8611 | -217315.8654 | -238634.1046 | -259445.1693 | -280247.781 | -301058.8456 | -321861.4573 | -342672.522 | -363475.1337 | -384286.1983 | -405088.81 | -425899.8747 | -446702.4864 | -467513.551 | -488316.1627 | -490268.785 | -473362.9648 | -456457.1446 | -439551.3245 | -422645.5043 | -405739.6841 | -388833.8639 | -371928.0438 | -355022.2236 | -338116.4034 | -321210.5833 | -304304.7631 | -287398.9429 | -270493.1227 | -253587.3026 | -236681.4824 | -219775.6622 | -202869.8421 | -185964.0219 | -169058.2017 | -152152.3815 | -135246.5614 | -118340.7412 | -101434.921 | -84529.1009 | -67623.2807 | -50717.4605 | -33811.6403 | -16905.8202 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10
|  |  | ADIT (e.o.y.) |  |  | -14792.5927 | -58908.3304 | -98442.5909 | -133750.3963 | -165136.0514 | -192903.8611 | -217315.8654 | -238634.1046 | -259445.1693 | -280247.781 | -301058.8456 | -321861.4573 | -342672.522 | -363475.1337 | -384286.1983 | -405088.81 | -425899.8747 | -446702.4864 | -467513.551 | -488316.1627 | -490268.785 | -473362.9648 | -456457.1446 | -439551.3245 | -422645.5043 | -405739.6841 | -388833.8639 | -371928.0438 | -355022.2236 | -338116.4034 | -321210.5833 | -304304.7631 | -287398.9429 | -270493.1227 | -253587.3026 | -236681.4824 | -219775.6622 | -202869.8421 | -185964.0219 | -169058.2017 | -152152.3815 | -135246.5614 | -118340.7412 | -101434.921 | -84529.1009 | -67623.2807 | -50717.4605 | -33811.6403 | -16905.8202 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10
|  |  | Net Rate Base |  |  | 3012044.7951 | 2921591.82 | 2818768.011 | 2720348.1681 | 2626002.6279 | 2535427.0855 | 2448338.3686 | 2364474.4369 | 2282410.9751 | 2200605.327 | 2118799.6789 | 2036994.0308 | 1955188.3826 | 1873382.7345 | 1791577.0864 | 1709771.4383 | 1627965.7902 | 1546160.1421 | 1464354.494 | 1382548.8459 | 1310172.419 | 1256650.2081 | 1212557.2183 | 1168464.2285 | 1124371.2388 | 1080278.249 | 1036185.2593 | 992092.2695 | 947999.2798 | 903906.29 | 859813.3003 | 815720.3105 | 771627.3207 | 727534.331 | 683441.3412 | 639348.3515 | 595255.3617 | 551162.372 | 507069.3822 | 462976.3924 | 418883.4027 | 374790.4129 | 330697.4232 | 286604.4334 | 242511.4437 | 198418.4539 | 154325.4641 | 110232.4744 | 66139.4846 | 22046.4949 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10 | -1.1642e-10
|  |  | Pre-Tax return on rate base |  |  | 268975.6002 | 260898.1495 | 251715.9834 | 242927.0914 | 234502.0347 | 226413.6387 | 218636.6163 | 211147.5672 | 203819.3001 | 196514.0557 | 189208.8113 | 181903.5669 | 174598.3226 | 167293.0782 | 159987.8338 | 152682.5894 | 145377.3451 | 138072.1007 | 130766.8563 | 123461.6119 | 116998.397 | 112218.8636 | 108281.3596 | 104343.8556 | 100406.3516 | 96468.8476 | 92531.3437 | 88593.8397 | 84656.3357 | 80718.8317 | 76781.3277 | 72843.8237 | 68906.3197 | 64968.8158 | 61031.3118 | 57093.8078 | 53156.3038 | 49218.7998 | 45281.2958 | 41343.7918 | 37406.2879 | 33468.7839 | 29531.2799 | 25593.7759 | 21656.2719 | 17718.7679 | 13781.2639 | 9843.76 | 5906.256 | 1968.752 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11 | -1.0396e-11
|  | Investment year in service |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98
QAQC check |  | 2029 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
3117039.1873 |  |  | Book depreciation |  |  |  | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 62340.7837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service |  |  | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 3117039.1873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation |  |  |  | -62340.7837 | -124681.5675 | -187022.3512 | -249363.135 | -311703.9187 | -374044.7025 | -436385.4862 | -498726.27 | -561067.0537 | -623407.8375 | -685748.6212 | -748089.405 | -810430.1887 | -872770.9724 | -935111.7562 | -997452.5399 | -1059793.3237 | -1122134.1074 | -1184474.8912 | -1246815.6749 | -1309156.4587 | -1371497.2424 | -1433838.0262 | -1496178.8099 | -1558519.5937 | -1620860.3774 | -1683201.1612 | -1745541.9449 | -1807882.7286 | -1870223.5124 | -1932564.2961 | -1994905.0799 | -2057245.8636 | -2119586.6474 | -2181927.4311 | -2244268.2149 | -2306608.9986 | -2368949.7824 | -2431290.5661 | -2493631.3499 | -2555972.1336 | -2618312.9173 | -2680653.7011 | -2742994.4848 | -2805335.2686 | -2867676.0523 | -2930016.8361 | -2992357.6198 | -3054698.4036 | -3117039.1873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) |  |  |  | 3117039.1873 | 3054698.4036 | 2992357.6198 | 2930016.8361 | 2867676.0523 | 2805335.2686 | 2742994.4848 | 2680653.7011 | 2618312.9173 | 2555972.1336 | 2493631.3499 | 2431290.5661 | 2368949.7824 | 2306608.9986 | 2244268.2149 | 2181927.4311 | 2119586.6474 | 2057245.8636 | 1994905.0799 | 1932564.2961 | 1870223.5124 | 1807882.7286 | 1745541.9449 | 1683201.1612 | 1620860.3774 | 1558519.5937 | 1496178.8099 | 1433838.0262 | 1371497.2424 | 1309156.4587 | 1246815.6749 | 1184474.8912 | 1122134.1074 | 1059793.3237 | 997452.5399 | 935111.7562 | 872770.9724 | 810430.1887 | 748089.405 | 685748.6212 | 623407.8375 | 561067.0537 | 498726.27 | 436385.4862 | 374044.7025 | 311703.9187 | 249363.135 | 187022.3512 | 124681.5675 | 62340.7837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) |  |  | 3117039.1873 | 3054698.4036 | 2992357.6198 | 2930016.8361 | 2867676.0523 | 2805335.2686 | 2742994.4848 | 2680653.7011 | 2618312.9173 | 2555972.1336 | 2493631.3499 | 2431290.5661 | 2368949.7824 | 2306608.9986 | 2244268.2149 | 2181927.4311 | 2119586.6474 | 2057245.8636 | 1994905.0799 | 1932564.2961 | 1870223.5124 | 1807882.7286 | 1745541.9449 | 1683201.1612 | 1620860.3774 | 1558519.5937 | 1496178.8099 | 1433838.0262 | 1371497.2424 | 1309156.4587 | 1246815.6749 | 1184474.8912 | 1122134.1074 | 1059793.3237 | 997452.5399 | 935111.7562 | 872770.9724 | 810430.1887 | 748089.405 | 685748.6212 | 623407.8375 | 561067.0537 | 498726.27 | 436385.4862 | 374044.7025 | 311703.9187 | 249363.135 | 187022.3512 | 124681.5675 | 62340.7837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation |  |  |  | 116888.9695 | 225019.0589 | 208124.7065 | 192539.5106 | 178076.4488 | 164735.521 | 152360.8755 | 140952.5121 | 139082.2885 | 139051.1181 | 139082.2885 | 139051.1181 | 139082.2885 | 139051.1181 | 139082.2885 | 139051.1181 | 139082.2885 | 139051.1181 | 139082.2885 | 139051.1181 | 69541.1443 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) |  |  |  | 0 | -15118.0297 | -60204.3137 | -100608.3279 | -136692.905 | -168769.0446 | -197147.746 | -222096.8144 | -243884.0549 | -265152.963 | -286413.2322 | -307682.1402 | -328942.4094 | -350211.3175 | -371471.5866 | -392740.4947 | -414000.7639 | -435269.6719 | -456529.9411 | -477798.8491 | -499059.1183 | -501054.6982 | -483776.95 | -466499.2018 | -449221.4536 | -431943.7054 | -414665.9572 | -397388.209 | -380110.4607 | -362832.7125 | -345554.9643 | -328277.2161 | -310999.4679 | -293721.7197 | -276443.9714 | -259166.2232 | -241888.475 | -224610.7268 | -207332.9786 | -190055.2304 | -172777.4822 | -155499.7339 | -138221.9857 | -120944.2375 | -103666.4893 | -86388.7411 | -69110.9929 | -51833.2446 | -34555.4964 | -17277.7482 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10
|  |  | ADIT (e.o.y.) |  |  |  | -15118.0297 | -60204.3137 | -100608.3279 | -136692.905 | -168769.0446 | -197147.746 | -222096.8144 | -243884.0549 | -265152.963 | -286413.2322 | -307682.1402 | -328942.4094 | -350211.3175 | -371471.5866 | -392740.4947 | -414000.7639 | -435269.6719 | -456529.9411 | -477798.8491 | -499059.1183 | -501054.6982 | -483776.95 | -466499.2018 | -449221.4536 | -431943.7054 | -414665.9572 | -397388.209 | -380110.4607 | -362832.7125 | -345554.9643 | -328277.2161 | -310999.4679 | -293721.7197 | -276443.9714 | -259166.2232 | -241888.475 | -224610.7268 | -207332.9786 | -190055.2304 | -172777.4822 | -155499.7339 | -138221.9857 | -120944.2375 | -103666.4893 | -86388.7411 | -69110.9929 | -51833.2446 | -34555.4964 | -17277.7482 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10
|  |  | Net Rate Base |  |  |  | 3078309.7806 | 2985866.84 | 2880780.9072 | 2780195.8278 | 2683774.6857 | 2591206.4814 | 2502201.8127 | 2416492.8745 | 2332624.0165 | 2249018.6442 | 2165413.2718 | 2081807.8994 | 1998202.5271 | 1914597.1547 | 1830991.7823 | 1747386.41 | 1663781.0376 | 1580175.6653 | 1496570.2929 | 1412964.9205 | 1338996.2122 | 1284296.5126 | 1239233.4771 | 1194170.4416 | 1149107.406 | 1104044.3705 | 1058981.335 | 1013918.2994 | 968855.2639 | 923792.2284 | 878729.1929 | 833666.1573 | 788603.1218 | 743540.0863 | 698477.0507 | 653414.0152 | 608350.9797 | 563287.9441 | 518224.9086 | 473161.8731 | 428098.8375 | 383035.802 | 337972.7665 | 292909.731 | 247846.6954 | 202783.6599 | 157720.6244 | 112657.5888 | 67594.5533 | 22531.5178 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10
|  |  | Pre-Tax return on rate base |  |  |  | 274893.0634 | 266637.9088 | 257253.735 | 248271.4874 | 239661.0794 | 231394.7388 | 223446.6219 | 215792.8137 | 208303.3247 | 200837.3649 | 193371.4052 | 185905.4454 | 178439.4857 | 170973.5259 | 163507.5662 | 156041.6064 | 148575.6467 | 141109.6869 | 133643.7272 | 126177.7674 | 119572.3618 | 114687.6786 | 110663.5495 | 106639.4204 | 102615.2914 | 98591.1623 | 94567.0332 | 90542.9041 | 86518.7751 | 82494.646 | 78470.5169 | 74446.3878 | 70422.2588 | 66398.1297 | 62374.0006 | 58349.8716 | 54325.7425 | 50301.6134 | 46277.4843 | 42253.3553 | 38229.2262 | 34205.0971 | 30180.968 | 26156.839 | 22132.7099 | 18108.5808 | 14084.4518 | 10060.3227 | 6036.1936 | 2012.0645 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11
|  | Investment year in service |  |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97
|  | 2030 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
|  |  | Book depreciation |  |  |  |  | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 63712.281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service |  |  |  | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 3185614.0494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation |  |  |  |  | -63712.281 | -127424.562 | -191136.843 | -254849.124 | -318561.4049 | -382273.6859 | -445985.9669 | -509698.2479 | -573410.5289 | -637122.8099 | -700835.0909 | -764547.3719 | -828259.6529 | -891971.9338 | -955684.2148 | -1019396.4958 | -1083108.7768 | -1146821.0578 | -1210533.3388 | -1274245.6198 | -1337957.9008 | -1401670.1818 | -1465382.4627 | -1529094.7437 | -1592807.0247 | -1656519.3057 | -1720231.5867 | -1783943.8677 | -1847656.1487 | -1911368.4297 | -1975080.7107 | -2038792.9916 | -2102505.2726 | -2166217.5536 | -2229929.8346 | -2293642.1156 | -2357354.3966 | -2421066.6776 | -2484778.9586 | -2548491.2396 | -2612203.5205 | -2675915.8015 | -2739628.0825 | -2803340.3635 | -2867052.6445 | -2930764.9255 | -2994477.2065 | -3058189.4875 | -3121901.7685 | -3185614.0494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) |  |  |  |  | 3185614.0494 | 3121901.7685 | 3058189.4875 | 2994477.2065 | 2930764.9255 | 2867052.6445 | 2803340.3635 | 2739628.0825 | 2675915.8015 | 2612203.5205 | 2548491.2396 | 2484778.9586 | 2421066.6776 | 2357354.3966 | 2293642.1156 | 2229929.8346 | 2166217.5536 | 2102505.2726 | 2038792.9916 | 1975080.7107 | 1911368.4297 | 1847656.1487 | 1783943.8677 | 1720231.5867 | 1656519.3057 | 1592807.0247 | 1529094.7437 | 1465382.4627 | 1401670.1818 | 1337957.9008 | 1274245.6198 | 1210533.3388 | 1146821.0578 | 1083108.7768 | 1019396.4958 | 955684.2148 | 891971.9338 | 828259.6529 | 764547.3719 | 700835.0909 | 637122.8099 | 573410.5289 | 509698.2479 | 445985.9669 | 382273.6859 | 318561.4049 | 254849.124 | 191136.843 | 127424.562 | 63712.281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) |  |  |  | 3185614.0494 | 3121901.7685 | 3058189.4875 | 2994477.2065 | 2930764.9255 | 2867052.6445 | 2803340.3635 | 2739628.0825 | 2675915.8015 | 2612203.5205 | 2548491.2396 | 2484778.9586 | 2421066.6776 | 2357354.3966 | 2293642.1156 | 2229929.8346 | 2166217.5536 | 2102505.2726 | 2038792.9916 | 1975080.7107 | 1911368.4297 | 1847656.1487 | 1783943.8677 | 1720231.5867 | 1656519.3057 | 1592807.0247 | 1529094.7437 | 1465382.4627 | 1401670.1818 | 1337957.9008 | 1274245.6198 | 1210533.3388 | 1146821.0578 | 1083108.7768 | 1019396.4958 | 955684.2148 | 891971.9338 | 828259.6529 | 764547.3719 | 700835.0909 | 637122.8099 | 573410.5289 | 509698.2479 | 445985.9669 | 382273.6859 | 318561.4049 | 254849.124 | 191136.843 | 127424.562 | 63712.281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation |  |  |  |  | 119460.5269 | 229969.4782 | 212703.4501 | 196775.3798 | 181994.1306 | 168359.7025 | 155712.8147 | 144053.4673 | 142142.0989 | 142110.2427 | 142142.0989 | 142110.2427 | 142142.0989 | 142110.2427 | 142142.0989 | 142110.2427 | 142142.0989 | 142110.2427 | 142142.0989 | 142110.2427 | 71071.0494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) |  |  |  |  | 0 | -15450.6263 | -61528.8086 | -102821.7111 | -139700.1489 | -172481.9635 | -201484.9964 | -226982.9444 | -249249.5041 | -270986.3282 | -292714.3233 | -314451.1473 | -336179.1424 | -357915.9664 | -379643.9615 | -401380.7856 | -423108.7807 | -444845.6047 | -466573.5998 | -488310.4238 | -510038.4189 | -512077.9016 | -494420.0429 | -476762.1843 | -459104.3256 | -441446.4669 | -423788.6082 | -406130.7495 | -388472.8909 | -370815.0322 | -353157.1735 | -335499.3148 | -317841.4562 | -300183.5975 | -282525.7388 | -264867.8801 | -247210.0215 | -229552.1628 | -211894.3041 | -194236.4454 | -176578.5868 | -158920.7281 | -141262.8694 | -123605.0107 | -105947.1521 | -88289.2934 | -70631.4347 | -52973.576 | -35315.7174 | -17657.8587 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10
|  |  | ADIT (e.o.y.) |  |  |  |  | -15450.6263 | -61528.8086 | -102821.7111 | -139700.1489 | -172481.9635 | -201484.9964 | -226982.9444 | -249249.5041 | -270986.3282 | -292714.3233 | -314451.1473 | -336179.1424 | -357915.9664 | -379643.9615 | -401380.7856 | -423108.7807 | -444845.6047 | -466573.5998 | -488310.4238 | -510038.4189 | -512077.9016 | -494420.0429 | -476762.1843 | -459104.3256 | -441446.4669 | -423788.6082 | -406130.7495 | -388472.8909 | -370815.0322 | -353157.1735 | -335499.3148 | -317841.4562 | -300183.5975 | -282525.7388 | -264867.8801 | -247210.0215 | -229552.1628 | -211894.3041 | -194236.4454 | -176578.5868 | -158920.7281 | -141262.8694 | -123605.0107 | -105947.1521 | -88289.2934 | -70631.4347 | -52973.576 | -35315.7174 | -17657.8587 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10
|  |  | Net Rate Base |  |  |  |  | 3146032.5958 | 3051555.9105 | 2944158.0872 | 2841360.136 | 2742817.7288 | 2648213.024 | 2557250.2526 | 2469655.7178 | 2383941.7449 | 2298497.0543 | 2213052.3638 | 2127607.6732 | 2042162.9827 | 1956718.2921 | 1871273.6016 | 1785828.911 | 1700384.2204 | 1614939.5299 | 1529494.8393 | 1444050.1488 | 1368454.1289 | 1312551.0359 | 1266496.6136 | 1220442.1913 | 1174387.769 | 1128333.3467 | 1082278.9244 | 1036224.502 | 990170.0797 | 944115.6574 | 898061.2351 | 852006.8128 | 805952.3905 | 759897.9682 | 713843.5458 | 667789.1235 | 621734.7012 | 575680.2789 | 529625.8566 | 483571.4343 | 437517.012 | 391462.5897 | 345408.1673 | 299353.745 | 253299.3227 | 207244.9004 | 161190.4781 | 115136.0558 | 69081.6335 | 23027.2112 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10 | -2.3283e-10
|  |  | Pre-Tax return on rate base |  |  |  |  | 280940.7108 | 272503.9428 | 262913.3172 | 253733.4601 | 244933.6232 | 236485.423 | 228362.4476 | 220540.2556 | 212885.9978 | 205255.787 | 197625.5761 | 189995.3652 | 182365.1544 | 174734.9435 | 167104.7326 | 159474.5218 | 151844.3109 | 144214.1 | 136583.8892 | 128953.6783 | 122202.9537 | 117210.8075 | 113098.1476 | 108985.4877 | 104872.8278 | 100760.1679 | 96647.5079 | 92534.848 | 88422.1881 | 84309.5282 | 80196.8683 | 76084.2084 | 71971.5485 | 67858.8886 | 63746.2286 | 59633.5687 | 55520.9088 | 51408.2489 | 47295.589 | 43182.9291 | 39070.2692 | 34957.6093 | 30844.9493 | 26732.2894 | 22619.6295 | 18506.9696 | 14394.3097 | 10281.6498 | 6168.9899 | 2056.33 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11 | -2.0792e-11
|  | Investment year in service | [5 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96
|  | 2031 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
|  |  | Book depreciation | [5 empty] | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 65113.9512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service |  |  |  |  | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 3255697.5585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation | [5 empty] | -65113.9512 | -130227.9023 | -195341.8535 | -260455.8047 | -325569.7559 | -390683.707 | -455797.6582 | -520911.6094 | -586025.5605 | -651139.5117 | -716253.4629 | -781367.414 | -846481.3652 | -911595.3164 | -976709.2676 | -1041823.2187 | -1106937.1699 | -1172051.1211 | -1237165.0722 | -1302279.0234 | -1367392.9746 | -1432506.9258 | -1497620.8769 | -1562734.8281 | -1627848.7793 | -1692962.7304 | -1758076.6816 | -1823190.6328 | -1888304.5839 | -1953418.5351 | -2018532.4863 | -2083646.4375 | -2148760.3886 | -2213874.3398 | -2278988.291 | -2344102.2421 | -2409216.1933 | -2474330.1445 | -2539444.0957 | -2604558.0468 | -2669671.998 | -2734785.9492 | -2799899.9003 | -2865013.8515 | -2930127.8027 | -2995241.7538 | -3060355.705 | -3125469.6562 | -3190583.6074 | -3255697.5585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) | [5 empty] | 3255697.5585 | 3190583.6074 | 3125469.6562 | 3060355.705 | 2995241.7538 | 2930127.8027 | 2865013.8515 | 2799899.9003 | 2734785.9492 | 2669671.998 | 2604558.0468 | 2539444.0957 | 2474330.1445 | 2409216.1933 | 2344102.2421 | 2278988.291 | 2213874.3398 | 2148760.3886 | 2083646.4375 | 2018532.4863 | 1953418.5351 | 1888304.5839 | 1823190.6328 | 1758076.6816 | 1692962.7304 | 1627848.7793 | 1562734.8281 | 1497620.8769 | 1432506.9258 | 1367392.9746 | 1302279.0234 | 1237165.0722 | 1172051.1211 | 1106937.1699 | 1041823.2187 | 976709.2676 | 911595.3164 | 846481.3652 | 781367.414 | 716253.4629 | 651139.5117 | 586025.5605 | 520911.6094 | 455797.6582 | 390683.707 | 325569.7559 | 260455.8047 | 195341.8535 | 130227.9023 | 65113.9512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) |  |  |  |  | 3255697.5585 | 3190583.6074 | 3125469.6562 | 3060355.705 | 2995241.7538 | 2930127.8027 | 2865013.8515 | 2799899.9003 | 2734785.9492 | 2669671.998 | 2604558.0468 | 2539444.0957 | 2474330.1445 | 2409216.1933 | 2344102.2421 | 2278988.291 | 2213874.3398 | 2148760.3886 | 2083646.4375 | 2018532.4863 | 1953418.5351 | 1888304.5839 | 1823190.6328 | 1758076.6816 | 1692962.7304 | 1627848.7793 | 1562734.8281 | 1497620.8769 | 1432506.9258 | 1367392.9746 | 1302279.0234 | 1237165.0722 | 1172051.1211 | 1106937.1699 | 1041823.2187 | 976709.2676 | 911595.3164 | 846481.3652 | 781367.414 | 716253.4629 | 651139.5117 | 586025.5605 | 520911.6094 | 455797.6582 | 390683.707 | 325569.7559 | 260455.8047 | 195341.8535 | 130227.9023 | 65113.9512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation | [5 empty] | 122088.6584 | 235028.8068 | 217382.926 | 201104.4382 | 185998.0015 | 172063.616 | 159138.4967 | 147222.6436 | 145269.2251 | 145236.6681 | 145269.2251 | 145236.6681 | 145269.2251 | 145236.6681 | 145269.2251 | 145236.6681 | 145269.2251 | 145236.6681 | 145269.2251 | 145236.6681 | 72634.6125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) | [5 empty] | 0 | -15790.5401 | -62882.4423 | -105083.7887 | -142773.5522 | -176276.5667 | -205917.6663 | -231976.5691 | -254732.9932 | -276948.0274 | -299154.0384 | -321369.0725 | -343575.0835 | -365790.1177 | -387996.1287 | -410211.1628 | -432417.1738 | -454632.208 | -476838.219 | -499053.2532 | -521259.2641 | -523343.6154 | -505297.2839 | -487250.9523 | -469204.6207 | -451158.2892 | -433111.9576 | -415065.626 | -397019.2945 | -378972.9629 | -360926.6313 | -342880.2998 | -324833.9682 | -306787.6366 | -288741.3051 | -270694.9735 | -252648.6419 | -234602.3104 | -216555.9788 | -198509.6472 | -180463.3157 | -162416.9841 | -144370.6525 | -126324.321 | -108277.9894 | -90231.6578 | -72185.3263 | -54138.9947 | -36092.6631 | -18046.3316 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10
|  |  | ADIT (e.o.y.) | [5 empty] | -15790.5401 | -62882.4423 | -105083.7887 | -142773.5522 | -176276.5667 | -205917.6663 | -231976.5691 | -254732.9932 | -276948.0274 | -299154.0384 | -321369.0725 | -343575.0835 | -365790.1177 | -387996.1287 | -410211.1628 | -432417.1738 | -454632.208 | -476838.219 | -499053.2532 | -521259.2641 | -523343.6154 | -505297.2839 | -487250.9523 | -469204.6207 | -451158.2892 | -433111.9576 | -415065.626 | -397019.2945 | -378972.9629 | -360926.6313 | -342880.2998 | -324833.9682 | -306787.6366 | -288741.3051 | -270694.9735 | -252648.6419 | -234602.3104 | -216555.9788 | -198509.6472 | -180463.3157 | -162416.9841 | -144370.6525 | -126324.321 | -108277.9894 | -90231.6578 | -72185.3263 | -54138.9947 | -36092.6631 | -18046.3316 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10
|  |  | Net Rate Base | [5 empty] | 3215245.3129 | 3118690.1405 | 3008929.5651 | 2903870.059 | 2803159.7188 | 2706473.7105 | 2613509.7582 | 2523988.1436 | 2436388.4633 | 2349063.9895 | 2261739.5158 | 2174415.042 | 2087090.5683 | 1999766.0945 | 1912441.6208 | 1825117.147 | 1737792.6733 | 1650468.1995 | 1563143.7258 | 1475819.2521 | 1398560.1197 | 1341427.1587 | 1294359.5391 | 1247291.9195 | 1200224.2999 | 1153156.6803 | 1106089.0607 | 1059021.4411 | 1011953.8215 | 964886.2019 | 917818.5823 | 870750.9627 | 823683.3431 | 776615.7235 | 729548.1039 | 682480.4843 | 635412.8646 | 588345.245 | 541277.6254 | 494210.0058 | 447142.3862 | 400074.7666 | 353007.147 | 305939.5274 | 258871.9078 | 211804.2882 | 164736.6686 | 117669.049 | 70601.4294 | 23533.8098 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10 | 4.0745e-10
|  |  | Pre-Tax return on rate base | [5 empty] | 287121.4064 | 278499.0296 | 268697.4102 | 259315.5963 | 250322.1629 | 241688.1024 | 233386.4214 | 225392.1412 | 217569.4898 | 209771.4143 | 201973.3388 | 194175.2633 | 186377.1877 | 178579.1122 | 170781.0367 | 162982.9612 | 155184.8857 | 147386.8102 | 139588.7347 | 131790.6592 | 124891.4187 | 119789.4453 | 115586.3068 | 111383.1684 | 107180.03 | 102976.8915 | 98773.7531 | 94570.6147 | 90367.4763 | 86164.3378 | 81961.1994 | 77758.061 | 73554.9225 | 69351.7841 | 65148.6457 | 60945.5072 | 56742.3688 | 52539.2304 | 48336.092 | 44132.9535 | 39929.8151 | 35726.6767 | 31523.5382 | 27320.3998 | 23117.2614 | 18914.1229 | 14710.9845 | 10507.8461 | 6304.7076 | 2101.5692 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11 | 3.6386e-11
|  | Investment year in service | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95
|  | 2032 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
|  |  | Book depreciation | [6 empty] | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 66546.4581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service | [5 empty] | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 3327322.9048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation | [6 empty] | -66546.4581 | -133092.9162 | -199639.3743 | -266185.8324 | -332732.2905 | -399278.7486 | -465825.2067 | -532371.6648 | -598918.1229 | -665464.581 | -732011.0391 | -798557.4972 | -865103.9553 | -931650.4133 | -998196.8714 | -1064743.3295 | -1131289.7876 | -1197836.2457 | -1264382.7038 | -1330929.1619 | -1397475.62 | -1464022.0781 | -1530568.5362 | -1597114.9943 | -1663661.4524 | -1730207.9105 | -1796754.3686 | -1863300.8267 | -1929847.2848 | -1996393.7429 | -2062940.201 | -2129486.6591 | -2196033.1172 | -2262579.5753 | -2329126.0334 | -2395672.4915 | -2462218.9496 | -2528765.4077 | -2595311.8658 | -2661858.3239 | -2728404.782 | -2794951.24 | -2861497.6981 | -2928044.1562 | -2994590.6143 | -3061137.0724 | -3127683.5305 | -3194229.9886 | -3260776.4467 | -3327322.9048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) | [6 empty] | 3327322.9048 | 3260776.4467 | 3194229.9886 | 3127683.5305 | 3061137.0724 | 2994590.6143 | 2928044.1562 | 2861497.6981 | 2794951.24 | 2728404.782 | 2661858.3239 | 2595311.8658 | 2528765.4077 | 2462218.9496 | 2395672.4915 | 2329126.0334 | 2262579.5753 | 2196033.1172 | 2129486.6591 | 2062940.201 | 1996393.7429 | 1929847.2848 | 1863300.8267 | 1796754.3686 | 1730207.9105 | 1663661.4524 | 1597114.9943 | 1530568.5362 | 1464022.0781 | 1397475.62 | 1330929.1619 | 1264382.7038 | 1197836.2457 | 1131289.7876 | 1064743.3295 | 998196.8714 | 931650.4133 | 865103.9553 | 798557.4972 | 732011.0391 | 665464.581 | 598918.1229 | 532371.6648 | 465825.2067 | 399278.7486 | 332732.2905 | 266185.8324 | 199639.3743 | 133092.9162 | 66546.4581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) | [5 empty] | 3327322.9048 | 3260776.4467 | 3194229.9886 | 3127683.5305 | 3061137.0724 | 2994590.6143 | 2928044.1562 | 2861497.6981 | 2794951.24 | 2728404.782 | 2661858.3239 | 2595311.8658 | 2528765.4077 | 2462218.9496 | 2395672.4915 | 2329126.0334 | 2262579.5753 | 2196033.1172 | 2129486.6591 | 2062940.201 | 1996393.7429 | 1929847.2848 | 1863300.8267 | 1796754.3686 | 1730207.9105 | 1663661.4524 | 1597114.9943 | 1530568.5362 | 1464022.0781 | 1397475.62 | 1330929.1619 | 1264382.7038 | 1197836.2457 | 1131289.7876 | 1064743.3295 | 998196.8714 | 931650.4133 | 865103.9553 | 798557.4972 | 732011.0391 | 665464.581 | 598918.1229 | 532371.6648 | 465825.2067 | 399278.7486 | 332732.2905 | 266185.8324 | 199639.3743 | 133092.9162 | 66546.4581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation | [6 empty] | 124774.6089 | 240199.4405 | 222165.3504 | 205528.7358 | 190089.9576 | 175849.0155 | 162639.5436 | 150461.5418 | 148465.148 | 148431.8748 | 148465.148 | 148431.8748 | 148465.148 | 148431.8748 | 148465.148 | 148431.8748 | 148465.148 | 148431.8748 | 148465.148 | 148431.8748 | 74232.574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) | [6 empty] | 0 | -16137.932 | -64265.8561 | -107395.6321 | -145914.5703 | -180154.6512 | -210447.855 | -237080.0536 | -260337.1191 | -283040.884 | -305735.4272 | -328439.1921 | -351133.7354 | -373837.5003 | -396532.0435 | -419235.8084 | -441930.3517 | -464634.1166 | -487328.6598 | -510032.4247 | -532726.968 | -534857.175 | -516413.8241 | -497970.4733 | -479527.1224 | -461083.7715 | -442640.4207 | -424197.0698 | -405753.719 | -387310.3681 | -368867.0172 | -350423.6664 | -331980.3155 | -313536.9646 | -295093.6138 | -276650.2629 | -258206.9121 | -239763.5612 | -221320.2103 | -202876.8595 | -184433.5086 | -165990.1578 | -147546.8069 | -129103.456 | -110660.1052 | -92216.7543 | -73773.4034 | -55330.0526 | -36886.7017 | -18443.3509 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10
|  |  | ADIT (e.o.y.) | [6 empty] | -16137.932 | -64265.8561 | -107395.6321 | -145914.5703 | -180154.6512 | -210447.855 | -237080.0536 | -260337.1191 | -283040.884 | -305735.4272 | -328439.1921 | -351133.7354 | -373837.5003 | -396532.0435 | -419235.8084 | -441930.3517 | -464634.1166 | -487328.6598 | -510032.4247 | -532726.968 | -534857.175 | -516413.8241 | -497970.4733 | -479527.1224 | -461083.7715 | -442640.4207 | -424197.0698 | -405753.719 | -387310.3681 | -368867.0172 | -350423.6664 | -331980.3155 | -313536.9646 | -295093.6138 | -276650.2629 | -258206.9121 | -239763.5612 | -221320.2103 | -202876.8595 | -184433.5086 | -165990.1578 | -147546.8069 | -129103.456 | -110660.1052 | -92216.7543 | -73773.4034 | -55330.0526 | -36886.7017 | -18443.3509 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10
|  |  | Net Rate Base | [6 empty] | 3285980.7098 | 3187301.3236 | 3075126.0155 | 2967755.2003 | 2864829.2326 | 2766016.1322 | 2671006.9729 | 2579515.8827 | 2489989.0095 | 2400743.3973 | 2311497.7851 | 2222252.173 | 2133006.5608 | 2043760.9486 | 1954515.3364 | 1865269.7243 | 1776024.1121 | 1686778.4999 | 1597532.8878 | 1508287.2756 | 1429328.4424 | 1370938.5562 | 1322835.449 | 1274732.3417 | 1226629.2345 | 1178526.1273 | 1130423.02 | 1082319.9128 | 1034216.8056 | 986113.6983 | 938010.5911 | 889907.4838 | 841804.3766 | 793701.2694 | 745598.1621 | 697495.0549 | 649391.9477 | 601288.8404 | 553185.7332 | 505082.626 | 456979.5187 | 408876.4115 | 360773.3043 | 312670.197 | 264567.0898 | 216463.9826 | 168360.8753 | 120257.7681 | 72154.6609 | 24051.5536 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10 | -5.0204e-10
|  |  | Pre-Tax return on rate base | [6 empty] | 293438.0774 | 284626.0082 | 274608.7532 | 265020.5394 | 255829.2505 | 247005.2406 | 238520.9227 | 230350.7683 | 222356.0185 | 214386.3854 | 206416.7522 | 198447.119 | 190477.4859 | 182507.8527 | 174538.2195 | 166568.5864 | 158598.9532 | 150629.32 | 142659.6869 | 134690.0537 | 127639.0299 | 122424.8131 | 118129.2056 | 113833.5981 | 109537.9906 | 105242.3832 | 100946.7757 | 96651.1682 | 92355.5607 | 88059.9533 | 83764.3458 | 79468.7383 | 75173.1308 | 70877.5234 | 66581.9159 | 62286.3084 | 57990.7009 | 53695.0935 | 49399.486 | 45103.8785 | 40808.271 | 36512.6635 | 32217.0561 | 27921.4486 | 23625.8411 | 19330.2336 | 15034.6262 | 10739.0187 | 6443.4112 | 2147.8037 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11 | -4.4832e-11
|  | Investment year in service | [7 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94
|  | 2033 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
|  |  | Book depreciation | [7 empty] | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 68010.4802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service | [6 empty] | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 3400524.0087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation | [7 empty] | -68010.4802 | -136020.9603 | -204031.4405 | -272041.9207 | -340052.4009 | -408062.881 | -476073.3612 | -544083.8414 | -612094.3216 | -680104.8017 | -748115.2819 | -816125.7621 | -884136.2423 | -952146.7224 | -1020157.2026 | -1088167.6828 | -1156178.163 | -1224188.6431 | -1292199.1233 | -1360209.6035 | -1428220.0837 | -1496230.5638 | -1564241.044 | -1632251.5242 | -1700262.0044 | -1768272.4845 | -1836282.9647 | -1904293.4449 | -1972303.9251 | -2040314.4052 | -2108324.8854 | -2176335.3656 | -2244345.8458 | -2312356.3259 | -2380366.8061 | -2448377.2863 | -2516387.7665 | -2584398.2466 | -2652408.7268 | -2720419.207 | -2788429.6872 | -2856440.1673 | -2924450.6475 | -2992461.1277 | -3060471.6079 | -3128482.088 | -3196492.5682 | -3264503.0484 | -3332513.5285 | -3400524.0087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) | [7 empty] | 3400524.0087 | 3332513.5285 | 3264503.0484 | 3196492.5682 | 3128482.088 | 3060471.6079 | 2992461.1277 | 2924450.6475 | 2856440.1673 | 2788429.6872 | 2720419.207 | 2652408.7268 | 2584398.2466 | 2516387.7665 | 2448377.2863 | 2380366.8061 | 2312356.3259 | 2244345.8458 | 2176335.3656 | 2108324.8854 | 2040314.4052 | 1972303.9251 | 1904293.4449 | 1836282.9647 | 1768272.4845 | 1700262.0044 | 1632251.5242 | 1564241.044 | 1496230.5638 | 1428220.0837 | 1360209.6035 | 1292199.1233 | 1224188.6431 | 1156178.163 | 1088167.6828 | 1020157.2026 | 952146.7224 | 884136.2423 | 816125.7621 | 748115.2819 | 680104.8017 | 612094.3216 | 544083.8414 | 476073.3612 | 408062.881 | 340052.4009 | 272041.9207 | 204031.4405 | 136020.9603 | 68010.4802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) | [6 empty] | 3400524.0087 | 3332513.5285 | 3264503.0484 | 3196492.5682 | 3128482.088 | 3060471.6079 | 2992461.1277 | 2924450.6475 | 2856440.1673 | 2788429.6872 | 2720419.207 | 2652408.7268 | 2584398.2466 | 2516387.7665 | 2448377.2863 | 2380366.8061 | 2312356.3259 | 2244345.8458 | 2176335.3656 | 2108324.8854 | 2040314.4052 | 1972303.9251 | 1904293.4449 | 1836282.9647 | 1768272.4845 | 1700262.0044 | 1632251.5242 | 1564241.044 | 1496230.5638 | 1428220.0837 | 1360209.6035 | 1292199.1233 | 1224188.6431 | 1156178.163 | 1088167.6828 | 1020157.2026 | 952146.7224 | 884136.2423 | 816125.7621 | 748115.2819 | 680104.8017 | 612094.3216 | 544083.8414 | 476073.3612 | 408062.881 | 340052.4009 | 272041.9207 | 204031.4405 | 136020.9603 | 68010.4802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation | [7 empty] | 127519.6503 | 245483.8282 | 227052.9881 | 210050.368 | 194271.9366 | 179717.6939 | 166217.6135 | 153771.6957 | 151731.3813 | 151697.376 | 151731.3813 | 151697.376 | 151731.3813 | 151697.376 | 151731.3813 | 151697.376 | 151731.3813 | 151697.376 | 151731.3813 | 151697.376 | 75865.6906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) | [7 empty] | 0 | -16492.9665 | -65679.7049 | -109758.336 | -149124.6909 | -184118.0535 | -215077.7078 | -242295.8148 | -266064.5357 | -289267.7834 | -312461.6066 | -335664.8544 | -358858.6776 | -382061.9253 | -405255.7485 | -428458.9962 | -451652.8194 | -474856.0671 | -498049.8903 | -521253.1381 | -544446.9613 | -546624.0328 | -527774.9282 | -508925.8237 | -490076.7191 | -471227.6145 | -452378.5099 | -433529.4053 | -414680.3008 | -395831.1962 | -376982.0916 | -358132.987 | -339283.8824 | -320434.7779 | -301585.6733 | -282736.5687 | -263887.4641 | -245038.3595 | -226189.255 | -207340.1504 | -188491.0458 | -169641.9412 | -150792.8366 | -131943.7321 | -113094.6275 | -94245.5229 | -75396.4183 | -56547.3137 | -37698.2092 | -18849.1046 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11
|  |  | ADIT (e.o.y.) | [7 empty] | -16492.9665 | -65679.7049 | -109758.336 | -149124.6909 | -184118.0535 | -215077.7078 | -242295.8148 | -266064.5357 | -289267.7834 | -312461.6066 | -335664.8544 | -358858.6776 | -382061.9253 | -405255.7485 | -428458.9962 | -451652.8194 | -474856.0671 | -498049.8903 | -521253.1381 | -544446.9613 | -546624.0328 | -527774.9282 | -508925.8237 | -490076.7191 | -471227.6145 | -452378.5099 | -433529.4053 | -414680.3008 | -395831.1962 | -376982.0916 | -358132.987 | -339283.8824 | -320434.7779 | -301585.6733 | -282736.5687 | -263887.4641 | -245038.3595 | -226189.255 | -207340.1504 | -188491.0458 | -169641.9412 | -150792.8366 | -131943.7321 | -113094.6275 | -94245.5229 | -75396.4183 | -56547.3137 | -37698.2092 | -18849.1046 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11
|  |  | Net Rate Base | [7 empty] | 3358272.2854 | 3257421.9528 | 3142778.7878 | 3033045.8147 | 2927855.4757 | 2826868.4871 | 2729769.1263 | 2636265.2321 | 2544768.7677 | 2453559.752 | 2362350.7364 | 2271141.7208 | 2179932.7051 | 2088723.6895 | 1997514.6738 | 1906305.6582 | 1815096.6426 | 1723887.6269 | 1632678.6113 | 1541469.5957 | 1460773.6681 | 1401099.2044 | 1351937.8288 | 1302776.4532 | 1253615.0776 | 1204453.7021 | 1155292.3265 | 1106130.9509 | 1056969.5753 | 1007808.1997 | 958646.8241 | 909485.4485 | 860324.0729 | 811162.6973 | 762001.3217 | 712839.9461 | 663678.5705 | 614517.1949 | 565355.8193 | 516194.4437 | 467033.0681 | 417871.6925 | 368710.317 | 319548.9414 | 270387.5658 | 221226.1902 | 172064.8146 | 122903.439 | 73742.0634 | 24580.6878 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11 | 2.9104e-11
|  |  | Pre-Tax return on rate base | [7 empty] | 299893.7151 | 290887.7804 | 280650.1458 | 270850.9913 | 261457.494 | 252439.3559 | 243768.383 | 235418.4852 | 227247.851 | 219102.8859 | 210957.9208 | 202812.9557 | 194667.9906 | 186523.0255 | 178378.0604 | 170233.0953 | 162088.1302 | 153943.1651 | 145798.2 | 137653.2349 | 130447.0886 | 125118.159 | 120728.0481 | 116337.9373 | 111947.8264 | 107557.7156 | 103167.6048 | 98777.4939 | 94387.3831 | 89997.2722 | 85607.1614 | 81217.0506 | 76826.9397 | 72436.8289 | 68046.718 | 63656.6072 | 59266.4963 | 54876.3855 | 50486.2747 | 46096.1638 | 41706.053 | 37315.9421 | 32925.8313 | 28535.7205 | 24145.6096 | 19755.4988 | 15365.3879 | 10975.2771 | 6585.1663 | 2195.0554 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12 | 2.599e-12
|  | Investment year in service | [8 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93
|  | 2034 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
|  |  | Book depreciation | [8 empty] | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 69506.7107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service | [7 empty] | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 3475335.5369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation | [8 empty] | -69506.7107 | -139013.4215 | -208520.1322 | -278026.843 | -347533.5537 | -417040.2644 | -486546.9752 | -556053.6859 | -625560.3966 | -695067.1074 | -764573.8181 | -834080.5289 | -903587.2396 | -973093.9503 | -1042600.6611 | -1112107.3718 | -1181614.0826 | -1251120.7933 | -1320627.504 | -1390134.2148 | -1459640.9255 | -1529147.6362 | -1598654.347 | -1668161.0577 | -1737667.7685 | -1807174.4792 | -1876681.1899 | -1946187.9007 | -2015694.6114 | -2085201.3221 | -2154708.0329 | -2224214.7436 | -2293721.4544 | -2363228.1651 | -2432734.8758 | -2502241.5866 | -2571748.2973 | -2641255.0081 | -2710761.7188 | -2780268.4295 | -2849775.1403 | -2919281.851 | -2988788.5617 | -3058295.2725 | -3127801.9832 | -3197308.694 | -3266815.4047 | -3336322.1154 | -3405828.8262 | -3475335.5369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) | [8 empty] | 3475335.5369 | 3405828.8262 | 3336322.1154 | 3266815.4047 | 3197308.694 | 3127801.9832 | 3058295.2725 | 2988788.5617 | 2919281.851 | 2849775.1403 | 2780268.4295 | 2710761.7188 | 2641255.0081 | 2571748.2973 | 2502241.5866 | 2432734.8758 | 2363228.1651 | 2293721.4544 | 2224214.7436 | 2154708.0329 | 2085201.3221 | 2015694.6114 | 1946187.9007 | 1876681.1899 | 1807174.4792 | 1737667.7685 | 1668161.0577 | 1598654.347 | 1529147.6362 | 1459640.9255 | 1390134.2148 | 1320627.504 | 1251120.7933 | 1181614.0826 | 1112107.3718 | 1042600.6611 | 973093.9503 | 903587.2396 | 834080.5289 | 764573.8181 | 695067.1074 | 625560.3966 | 556053.6859 | 486546.9752 | 417040.2644 | 347533.5537 | 278026.843 | 208520.1322 | 139013.4215 | 69506.7107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) | [7 empty] | 3475335.5369 | 3405828.8262 | 3336322.1154 | 3266815.4047 | 3197308.694 | 3127801.9832 | 3058295.2725 | 2988788.5617 | 2919281.851 | 2849775.1403 | 2780268.4295 | 2710761.7188 | 2641255.0081 | 2571748.2973 | 2502241.5866 | 2432734.8758 | 2363228.1651 | 2293721.4544 | 2224214.7436 | 2154708.0329 | 2085201.3221 | 2015694.6114 | 1946187.9007 | 1876681.1899 | 1807174.4792 | 1737667.7685 | 1668161.0577 | 1598654.347 | 1529147.6362 | 1459640.9255 | 1390134.2148 | 1320627.504 | 1251120.7933 | 1181614.0826 | 1112107.3718 | 1042600.6611 | 973093.9503 | 903587.2396 | 834080.5289 | 764573.8181 | 695067.1074 | 625560.3966 | 556053.6859 | 486546.9752 | 417040.2644 | 347533.5537 | 278026.843 | 208520.1322 | 139013.4215 | 69506.7107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation | [8 empty] | 130325.0826 | 250884.4724 | 232048.1538 | 214671.4761 | 198545.9192 | 183671.4831 | 169874.401 | 157154.673 | 155069.4717 | 155034.7183 | 155069.4717 | 155034.7183 | 155069.4717 | 155034.7183 | 155069.4717 | 155034.7183 | 155069.4717 | 155034.7183 | 155069.4717 | 155034.7183 | 77534.7358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) | [8 empty] | 0 | -16855.8118 | -67124.6584 | -112173.0194 | -152405.4341 | -188168.6507 | -219809.4174 | -247626.3228 | -271917.9555 | -295631.6747 | -319335.762 | -343049.4812 | -366753.5685 | -390467.2876 | -414171.3749 | -437885.0941 | -461589.1814 | -485302.9006 | -509006.9879 | -532720.7071 | -556424.7944 | -558649.7616 | -539385.9767 | -520122.1918 | -500858.4069 | -481594.622 | -462330.8371 | -443067.0523 | -423803.2674 | -404539.4825 | -385275.6976 | -366011.9127 | -346748.1279 | -327484.343 | -308220.5581 | -288956.7732 | -269692.9883 | -250429.2035 | -231165.4186 | -211901.6337 | -192637.8488 | -173374.0639 | -154110.279 | -134846.4942 | -115582.7093 | -96318.9244 | -77055.1395 | -57791.3546 | -38527.5698 | -19263.7849 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11
|  |  | ADIT (e.o.y.) | [8 empty] | -16855.8118 | -67124.6584 | -112173.0194 | -152405.4341 | -188168.6507 | -219809.4174 | -247626.3228 | -271917.9555 | -295631.6747 | -319335.762 | -343049.4812 | -366753.5685 | -390467.2876 | -414171.3749 | -437885.0941 | -461589.1814 | -485302.9006 | -509006.9879 | -532720.7071 | -556424.7944 | -558649.7616 | -539385.9767 | -520122.1918 | -500858.4069 | -481594.622 | -462330.8371 | -443067.0523 | -423803.2674 | -404539.4825 | -385275.6976 | -366011.9127 | -346748.1279 | -327484.343 | -308220.5581 | -288956.7732 | -269692.9883 | -250429.2035 | -231165.4186 | -211901.6337 | -192637.8488 | -173374.0639 | -154110.279 | -134846.4942 | -115582.7093 | -96318.9244 | -77055.1395 | -57791.3546 | -38527.5698 | -19263.7849 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11
|  |  | Net Rate Base | [8 empty] | 3432154.2757 | 3329085.2357 | 3211919.9212 | 3099772.8226 | 2992268.2962 | 2889059.5938 | 2789824.047 | 2694263.0673 | 2600753.6806 | 2507538.0666 | 2414322.4526 | 2321106.8386 | 2227891.2246 | 2134675.6107 | 2041459.9967 | 1948244.3827 | 1855028.7687 | 1761813.1547 | 1668597.5407 | 1575381.9268 | 1492910.6888 | 1431923.3869 | 1381680.4611 | 1331437.5352 | 1281194.6094 | 1230951.6835 | 1180708.7576 | 1130465.8318 | 1080222.9059 | 1029979.9801 | 979737.0542 | 929494.1284 | 879251.2025 | 829008.2766 | 778765.3508 | 728522.4249 | 678279.4991 | 628036.5732 | 577793.6474 | 527550.7215 | 477307.7956 | 427064.8698 | 376821.9439 | 326579.0181 | 276336.0922 | 226093.1664 | 175850.2405 | 125607.3146 | 75364.3888 | 25121.4629 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11 | -8.7311e-11
|  |  | Pre-Tax return on rate base | [8 empty] | 306491.3768 | 297287.3115 | 286824.449 | 276809.7131 | 267209.5588 | 257993.0217 | 249131.2874 | 240597.6919 | 232247.3037 | 223923.1493 | 215598.995 | 207274.8407 | 198950.6864 | 190626.532 | 182302.3777 | 173978.2234 | 165654.069 | 157329.9147 | 149005.7604 | 140681.6061 | 133316.9245 | 127870.7585 | 123384.0652 | 118897.3719 | 114410.6786 | 109923.9853 | 105437.2921 | 100950.5988 | 96463.9055 | 91977.2122 | 87490.5189 | 83003.8257 | 78517.1324 | 74030.4391 | 69543.7458 | 65057.0525 | 60570.3593 | 56083.666 | 51596.9727 | 47110.2794 | 42623.5862 | 38136.8929 | 33650.1996 | 29163.5063 | 24676.813 | 20190.1198 | 15703.4265 | 11216.7332 | 6730.0399 | 2243.3466 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12 | -7.7969e-12
|  | Investment year in service | [9 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92
|  | 2035 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
|  |  | Book depreciation | [9 empty] | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 71035.8584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service | [8 empty] | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 3551792.9187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation | [9 empty] | -71035.8584 | -142071.7167 | -213107.5751 | -284143.4335 | -355179.2919 | -426215.1502 | -497251.0086 | -568286.867 | -639322.7254 | -710358.5837 | -781394.4421 | -852430.3005 | -923466.1589 | -994502.0172 | -1065537.8756 | -1136573.734 | -1207609.5924 | -1278645.4507 | -1349681.3091 | -1420717.1675 | -1491753.0259 | -1562788.8842 | -1633824.7426 | -1704860.601 | -1775896.4594 | -1846932.3177 | -1917968.1761 | -1989004.0345 | -2060039.8929 | -2131075.7512 | -2202111.6096 | -2273147.468 | -2344183.3264 | -2415219.1847 | -2486255.0431 | -2557290.9015 | -2628326.7599 | -2699362.6182 | -2770398.4766 | -2841434.335 | -2912470.1934 | -2983506.0517 | -3054541.9101 | -3125577.7685 | -3196613.6269 | -3267649.4852 | -3338685.3436 | -3409721.202 | -3480757.0604 | -3551792.9187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) | [9 empty] | 3551792.9187 | 3480757.0604 | 3409721.202 | 3338685.3436 | 3267649.4852 | 3196613.6269 | 3125577.7685 | 3054541.9101 | 2983506.0517 | 2912470.1934 | 2841434.335 | 2770398.4766 | 2699362.6182 | 2628326.7599 | 2557290.9015 | 2486255.0431 | 2415219.1847 | 2344183.3264 | 2273147.468 | 2202111.6096 | 2131075.7512 | 2060039.8929 | 1989004.0345 | 1917968.1761 | 1846932.3177 | 1775896.4594 | 1704860.601 | 1633824.7426 | 1562788.8842 | 1491753.0259 | 1420717.1675 | 1349681.3091 | 1278645.4507 | 1207609.5924 | 1136573.734 | 1065537.8756 | 994502.0172 | 923466.1589 | 852430.3005 | 781394.4421 | 710358.5837 | 639322.7254 | 568286.867 | 497251.0086 | 426215.1502 | 355179.2919 | 284143.4335 | 213107.5751 | 142071.7167 | 71035.8584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) | [8 empty] | 3551792.9187 | 3480757.0604 | 3409721.202 | 3338685.3436 | 3267649.4852 | 3196613.6269 | 3125577.7685 | 3054541.9101 | 2983506.0517 | 2912470.1934 | 2841434.335 | 2770398.4766 | 2699362.6182 | 2628326.7599 | 2557290.9015 | 2486255.0431 | 2415219.1847 | 2344183.3264 | 2273147.468 | 2202111.6096 | 2131075.7512 | 2060039.8929 | 1989004.0345 | 1917968.1761 | 1846932.3177 | 1775896.4594 | 1704860.601 | 1633824.7426 | 1562788.8842 | 1491753.0259 | 1420717.1675 | 1349681.3091 | 1278645.4507 | 1207609.5924 | 1136573.734 | 1065537.8756 | 994502.0172 | 923466.1589 | 852430.3005 | 781394.4421 | 710358.5837 | 639322.7254 | 568286.867 | 497251.0086 | 426215.1502 | 355179.2919 | 284143.4335 | 213107.5751 | 142071.7167 | 71035.8584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation | [9 empty] | 133192.2345 | 256403.9308 | 237153.2132 | 219394.2486 | 202913.9294 | 187712.2558 | 173611.6379 | 160612.0758 | 158481 | 158445.4821 | 158481 | 158445.4821 | 158481 | 158445.4821 | 158481 | 158445.4821 | 158481 | 158445.4821 | 158481 | 158445.4821 | 79240.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) | [9 empty] | 0 | -17226.6396 | -68601.4009 | -114640.8258 | -155758.3536 | -192308.361 | -224645.2246 | -253074.1019 | -277900.1505 | -302135.5715 | -326361.1487 | -350596.5697 | -374822.147 | -399057.568 | -423283.1452 | -447518.5662 | -471744.1434 | -495979.5644 | -520205.1416 | -544440.5627 | -568666.1399 | -570940.0563 | -551252.4682 | -531564.88 | -511877.2919 | -492189.7037 | -472502.1156 | -452814.5274 | -433126.9393 | -413439.3511 | -393751.763 | -374064.1748 | -354376.5867 | -334688.9985 | -315001.4104 | -295313.8222 | -275626.2341 | -255938.6459 | -236251.0578 | -216563.4696 | -196875.8815 | -177188.2933 | -157500.7052 | -137813.117 | -118125.5289 | -98437.9407 | -78750.3526 | -59062.7644 | -39375.1763 | -19687.5881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (e.o.y.) | [9 empty] | -17226.6396 | -68601.4009 | -114640.8258 | -155758.3536 | -192308.361 | -224645.2246 | -253074.1019 | -277900.1505 | -302135.5715 | -326361.1487 | -350596.5697 | -374822.147 | -399057.568 | -423283.1452 | -447518.5662 | -471744.1434 | -495979.5644 | -520205.1416 | -544440.5627 | -568666.1399 | -570940.0563 | -551252.4682 | -531564.88 | -511877.2919 | -492189.7037 | -472502.1156 | -452814.5274 | -433126.9393 | -413439.3511 | -393751.763 | -374064.1748 | -354376.5867 | -334688.9985 | -315001.4104 | -295313.8222 | -275626.2341 | -255938.6459 | -236251.0578 | -216563.4696 | -196875.8815 | -177188.2933 | -157500.7052 | -137813.117 | -118125.5289 | -98437.9407 | -78750.3526 | -59062.7644 | -39375.1763 | -19687.5881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Rate Base | [9 empty] | 3507661.6697 | 3402325.1109 | 3282582.1594 | 3167967.8247 | 3058098.1987 | 2952618.9049 | 2851200.1761 | 2753536.8547 | 2657970.2615 | 2562703.904 | 2467437.5466 | 2372171.1891 | 2276904.8316 | 2181638.4741 | 2086372.1166 | 1991105.7591 | 1895839.4016 | 1800573.0441 | 1705306.6866 | 1610040.3292 | 1525754.724 | 1463425.7014 | 1412077.4312 | 1360729.161 | 1309380.8908 | 1258032.6205 | 1206684.3503 | 1155336.0801 | 1103987.8099 | 1052639.5396 | 1001291.2694 | 949942.9992 | 898594.729 | 847246.4587 | 795898.1885 | 744549.9183 | 693201.6481 | 641853.3778 | 590505.1076 | 539156.8374 | 487808.5671 | 436460.2969 | 385112.0267 | 333763.7565 | 282415.4862 | 231067.216 | 179718.9458 | 128370.6756 | 77022.4053 | 25674.1351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Pre-Tax return on rate base | [9 empty] | 313234.1871 | 303827.6324 | 293134.5868 | 282899.5267 | 273088.1691 | 263668.8682 | 254612.1757 | 245890.8411 | 237356.7444 | 228849.4586 | 220342.1729 | 211834.8872 | 203327.6015 | 194820.3157 | 186313.03 | 177805.7443 | 169298.4586 | 160791.1728 | 152283.8871 | 143776.6014 | 136249.8968 | 130683.9151 | 126098.5146 | 121513.1141 | 116927.7135 | 112342.313 | 107756.9125 | 103171.512 | 98586.1114 | 94000.7109 | 89415.3104 | 84829.9098 | 80244.5093 | 75659.1088 | 71073.7082 | 66488.3077 | 61902.9072 | 57317.5066 | 52732.1061 | 48146.7056 | 43561.305 | 38975.9045 | 34390.504 | 29805.1035 | 25219.7029 | 20634.3024 | 16048.9019 | 11463.5013 | 6878.1008 | 2292.7003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Investment year in service | [10 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91
|  | 2036 | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
|  |  | Book depreciation | [10 empty] | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 72598.6473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service | [9 empty] | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 3629932.3629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation | [10 empty] | -72598.6473 | -145197.2945 | -217795.9418 | -290394.589 | -362993.2363 | -435591.8836 | -508190.5308 | -580789.1781 | -653387.8253 | -725986.4726 | -798585.1198 | -871183.7671 | -943782.4144 | -1016381.0616 | -1088979.7089 | -1161578.3561 | -1234177.0034 | -1306775.6507 | -1379374.2979 | -1451972.9452 | -1524571.5924 | -1597170.2397 | -1669768.887 | -1742367.5342 | -1814966.1815 | -1887564.8287 | -1960163.476 | -2032762.1232 | -2105360.7705 | -2177959.4178 | -2250558.065 | -2323156.7123 | -2395755.3595 | -2468354.0068 | -2540952.6541 | -2613551.3013 | -2686149.9486 | -2758748.5958 | -2831347.2431 | -2903945.8904 | -2976544.5376 | -3049143.1849 | -3121741.8321 | -3194340.4794 | -3266939.1266 | -3339537.7739 | -3412136.4212 | -3484735.0684 | -3557333.7157 | -3629932.3629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) | [10 empty] | 3629932.3629 | 3557333.7157 | 3484735.0684 | 3412136.4212 | 3339537.7739 | 3266939.1266 | 3194340.4794 | 3121741.8321 | 3049143.1849 | 2976544.5376 | 2903945.8904 | 2831347.2431 | 2758748.5958 | 2686149.9486 | 2613551.3013 | 2540952.6541 | 2468354.0068 | 2395755.3595 | 2323156.7123 | 2250558.065 | 2177959.4178 | 2105360.7705 | 2032762.1232 | 1960163.476 | 1887564.8287 | 1814966.1815 | 1742367.5342 | 1669768.887 | 1597170.2397 | 1524571.5924 | 1451972.9452 | 1379374.2979 | 1306775.6507 | 1234177.0034 | 1161578.3561 | 1088979.7089 | 1016381.0616 | 943782.4144 | 871183.7671 | 798585.1198 | 725986.4726 | 653387.8253 | 580789.1781 | 508190.5308 | 435591.8836 | 362993.2363 | 290394.589 | 217795.9418 | 145197.2945 | 72598.6473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) | [9 empty] | 3629932.3629 | 3557333.7157 | 3484735.0684 | 3412136.4212 | 3339537.7739 | 3266939.1266 | 3194340.4794 | 3121741.8321 | 3049143.1849 | 2976544.5376 | 2903945.8904 | 2831347.2431 | 2758748.5958 | 2686149.9486 | 2613551.3013 | 2540952.6541 | 2468354.0068 | 2395755.3595 | 2323156.7123 | 2250558.065 | 2177959.4178 | 2105360.7705 | 2032762.1232 | 1960163.476 | 1887564.8287 | 1814966.1815 | 1742367.5342 | 1669768.887 | 1597170.2397 | 1524571.5924 | 1451972.9452 | 1379374.2979 | 1306775.6507 | 1234177.0034 | 1161578.3561 | 1088979.7089 | 1016381.0616 | 943782.4144 | 871183.7671 | 798585.1198 | 725986.4726 | 653387.8253 | 580789.1781 | 508190.5308 | 435591.8836 | 362993.2363 | 290394.589 | 217795.9418 | 145197.2945 | 72598.6473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation | [10 empty] | 136122.4636 | 262044.8173 | 242370.5839 | 224220.9221 | 207378.0359 | 191841.9254 | 177431.0939 | 164145.5415 | 161967.582 | 161931.2827 | 161967.582 | 161931.2827 | 161967.582 | 161931.2827 | 161967.582 | 161931.2827 | 161967.582 | 161931.2827 | 161967.582 | 161931.2827 | 80983.791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) | [10 empty] | 0 | -17605.6257 | -70110.6317 | -117162.924 | -159185.0374 | -196539.145 | -229587.4195 | -258641.7321 | -284013.9538 | -308782.5541 | -333541.094 | -358309.6943 | -383068.2342 | -407836.8345 | -432595.3744 | -457363.9747 | -482122.5146 | -506891.1148 | -531649.6548 | -556418.255 | -581176.795 | -583500.7375 | -563380.0225 | -543259.3074 | -523138.5923 | -503017.8772 | -482897.1621 | -462776.447 | -442655.7319 | -422535.0168 | -402414.3018 | -382293.5867 | -362172.8716 | -342052.1565 | -321931.4414 | -301810.7263 | -281690.0112 | -261569.2961 | -241448.5811 | -221327.866 | -201207.1509 | -181086.4358 | -160965.7207 | -140845.0056 | -120724.2905 | -100603.5754 | -80482.8604 | -60362.1453 | -40241.4302 | -20120.7151 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10
|  |  | ADIT (e.o.y.) | [10 empty] | -17605.6257 | -70110.6317 | -117162.924 | -159185.0374 | -196539.145 | -229587.4195 | -258641.7321 | -284013.9538 | -308782.5541 | -333541.094 | -358309.6943 | -383068.2342 | -407836.8345 | -432595.3744 | -457363.9747 | -482122.5146 | -506891.1148 | -531649.6548 | -556418.255 | -581176.795 | -583500.7375 | -563380.0225 | -543259.3074 | -523138.5923 | -503017.8772 | -482897.1621 | -462776.447 | -442655.7319 | -422535.0168 | -402414.3018 | -382293.5867 | -362172.8716 | -342052.1565 | -321931.4414 | -301810.7263 | -281690.0112 | -261569.2961 | -241448.5811 | -221327.866 | -201207.1509 | -181086.4358 | -160965.7207 | -140845.0056 | -120724.2905 | -100603.5754 | -80482.8604 | -60362.1453 | -40241.4302 | -20120.7151 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10
|  |  | Net Rate Base | [10 empty] | 3584830.2265 | 3477176.2633 | 3354798.967 | 3237663.1168 | 3125376.3591 | 3017576.5208 | 2913926.58 | 2814114.6655 | 2716445.6073 | 2619083.3899 | 2521721.1726 | 2424358.9552 | 2326996.7379 | 2229634.5205 | 2132272.3032 | 2034910.0858 | 1937547.8685 | 1840185.6511 | 1742823.4338 | 1645461.2164 | 1559321.3279 | 1495621.0669 | 1443143.1347 | 1390665.2025 | 1338187.2704 | 1285709.3382 | 1233231.406 | 1180753.4738 | 1128275.5417 | 1075797.6095 | 1023319.6773 | 970841.7452 | 918363.813 | 865885.8808 | 813407.9487 | 760930.0165 | 708452.0843 | 655974.1521 | 603496.22 | 551018.2878 | 498540.3556 | 446062.4235 | 393584.4913 | 341106.5591 | 288628.6269 | 236150.6948 | 183672.7626 | 131194.8304 | 78716.8983 | 26238.9661 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10 | -1.3824e-10
|  |  | Pre-Tax return on rate base | [10 empty] | 320125.3392 | 310511.8403 | 299583.5477 | 289123.3163 | 279096.1089 | 269469.5833 | 260213.6436 | 251300.4396 | 242578.5927 | 233884.1467 | 225189.7007 | 216495.2547 | 207800.8087 | 199106.3627 | 190411.9167 | 181717.4707 | 173023.0247 | 164328.5786 | 155634.1326 | 146939.6866 | 139247.3946 | 133558.9613 | 128872.6819 | 124186.4026 | 119500.1232 | 114813.8439 | 110127.5646 | 105441.2852 | 100755.0059 | 96068.7265 | 91382.4472 | 86696.1678 | 82009.8885 | 77323.6092 | 72637.3298 | 67951.0505 | 63264.7711 | 58578.4918 | 53892.2124 | 49205.9331 | 44519.6538 | 39833.3744 | 35147.0951 | 30460.8157 | 25774.5364 | 21088.257 | 16401.9777 | 11715.6984 | 7029.419 | 2343.1397 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11 | -1.2345e-11
|  |  | Total CAPEX cost rollup |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100
|  |  | CAPEX Cost element | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110 | 2111 | 2112 | 2113 | 2114 | 2115 | 2116 | 2117 | 2118 | 2119 | 2120 | 2121 | 2122 | 2123 | 2124 | 2125 | 2126 | 2127
|  |  | Book depreciation | 0 | 59685.724 | 120684.5339 | 183025.3177 | 246737.5987 | 311851.5498 | 378398.0079 | 446408.4881 | 515915.1988 | 586951.0572 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 659549.7045 | 599863.9805 | 538865.1705 | 476524.3868 | 412812.1058 | 347698.1546 | 281151.6965 | 213141.2164 | 143634.5056 | 72598.6473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Plant in Service | 2984286.2 | 2984286.2 | 6034226.6964 | 9151265.8837 | 12336879.9332 | 15592577.4917 | 18919900.3965 | 22320424.4052 | 25795759.9421 | 25795759.9421 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 32977485.2238 | 29993199.0238 | 26943258.5274 | 23826219.3401 | 20640605.2907 | 17384907.7321 | 14057584.8273 | 10657060.8186 | 7181725.2817 | 3629932.3629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Accumulated Depreciation | 0 | -59685.724 | -180370.2579 | -363395.5756 | -610133.1743 | -921984.7241 | -1300382.732 | -1746791.2201 | -2262706.419 | -2849657.4762 | -3509207.1807 | -4168756.8851 | -4828306.5896 | -5487856.2941 | -6147405.9986 | -6806955.7031 | -7466505.4075 | -8126055.112 | -8785604.8165 | -9445154.521 | -10104704.2254 | -10764253.9299 | -11423803.6344 | -12083353.3389 | -12742903.0433 | -13402452.7478 | -14062002.4523 | -14721552.1568 | -15381101.8612 | -16040651.5657 | -16700201.2702 | -17359750.9747 | -18019300.6791 | -18678850.3836 | -19338400.0881 | -19997949.7926 | -20657499.4971 | -21317049.2015 | -21976598.906 | -22636148.6105 | -23295698.315 | -23955248.0194 | -24614797.7239 | -25274347.4284 | -25933897.1329 | -26593446.8373 | -27252996.5418 | -27912546.2463 | -28572095.9508 | -29231645.6552 | -29891195.3597 | -27506773.1402 | -24995697.8143 | -22355183.0138 | -19582381.0702 | -16674381.6663 | -13628210.458 | -10440827.6657 | -7109126.6344 | -3629932.3629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (b.o.y.) | 0 | 2984286.2 | 5974540.9724 | 8970895.6258 | 11973484.3576 | 14982444.3174 | 17997915.6724 | 21020041.6732 | 24048968.722 | 27084846.4419 | 30127827.7476 | 29468278.0431 | 28808728.3387 | 28149178.6342 | 27489628.9297 | 26830079.2252 | 26170529.5208 | 25510979.8163 | 24851430.1118 | 24191880.4073 | 23532330.7029 | 22872780.9984 | 22213231.2939 | 21553681.5894 | 20894131.885 | 20234582.1805 | 19575032.476 | 18915482.7715 | 18255933.067 | 17596383.3626 | 16936833.6581 | 16277283.9536 | 15617734.2491 | 14958184.5447 | 14298634.8402 | 13639085.1357 | 12979535.4312 | 12319985.7268 | 11660436.0223 | 11000886.3178 | 10341336.6133 | 9681786.9089 | 9022237.2044 | 8362687.4999 | 7703137.7954 | 7043588.0909 | 6384038.3865 | 5724488.682 | 5064938.9775 | 4405389.273 | 3745839.5686 | 3086289.8641 | 2486425.8836 | 1947560.7131 | 1471036.3263 | 1058224.2205 | 710526.0658 | 429374.3693 | 216233.1529 | 72598.6473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Net Plant (e.o.y.) | 2984286.2 | 5974540.9724 | 8970895.6258 | 11973484.3576 | 14982444.3174 | 17997915.6724 | 21020041.6732 | 24048968.722 | 27084846.4419 | 30127827.7476 | 29468278.0431 | 28808728.3387 | 28149178.6342 | 27489628.9297 | 26830079.2252 | 26170529.5208 | 25510979.8163 | 24851430.1118 | 24191880.4073 | 23532330.7029 | 22872780.9984 | 22213231.2939 | 21553681.5894 | 20894131.885 | 20234582.1805 | 19575032.476 | 18915482.7715 | 18255933.067 | 17596383.3626 | 16936833.6581 | 16277283.9536 | 15617734.2491 | 14958184.5447 | 14298634.8402 | 13639085.1357 | 12979535.4312 | 12319985.7268 | 11660436.0223 | 11000886.3178 | 10341336.6133 | 9681786.9089 | 9022237.2044 | 8362687.4999 | 7703137.7954 | 7043588.0909 | 6384038.3865 | 5724488.682 | 5064938.9775 | 4405389.273 | 3745839.5686 | 3086289.8641 | 2486425.8836 | 1947560.7131 | 1471036.3263 | 1058224.2205 | 710526.0658 | 429374.3693 | 216233.1529 | 72598.6473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | MACRS depreciation | 0 | 111910.7325 | 329808.3894 | 536324.9635 | 732463.4713 | 919069.9383 | 1097009.0026 | 1267015.1101 | 1429838.8645 | 1594454.1698 | 1762661.1689 | 1795481.407 | 1700301.2021 | 1623163.9421 | 1562848.7738 | 1518449.9444 | 1488922.4028 | 1473502.968 | 1471292.2973 | 1471288.7092 | 1471292.2973 | 1404709.2841 | 1270119.1174 | 1132530.8692 | 991952.7774 | 848244.8696 | 701412.4858 | 551312.6917 | 397947.8 | 241171.7827 | 80983.791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | ADIT (b.o.y.) | 0 | 0 | -14474.1611 | -72432.8376 | -170349.8345 | -304968.7601 | -473259.3365 | -672422.3736 | -899853.4989 | -1153147.4429 | -1432376.9305 | -1738104.2728 | -2052927.7442 | -2341372.0218 | -2608437.7077 | -2858787.0448 | -3096831.2463 | -3326691.8896 | -3552279.0366 | -3777253.4962 | -4002226.9614 | -4227201.421 | -4433722.3985 | -4602941.7113 | -4734028.4411 | -4826153.9527 | -4878450.8178 | -4890053.0876 | -4860055.1995 | -4787552.2317 | -4671598.7907 | -4511249.2477 | -4328455.0471 | -4145660.8466 | -3962866.646 | -3780072.4454 | -3597278.2448 | -3414484.0442 | -3231689.8436 | -3048895.643 | -2866101.4424 | -2683307.2418 | -2500513.0412 | -2317718.8406 | -2134924.64 | -1952130.4394 | -1769336.2388 | -1586542.0382 | -1403747.8376 | -1220953.637 | -1038159.4364 | -855365.2358 | -689112.9336 | -539766.4516 | -407697.7178 | -293286.8427 | -196922.2991 | -119001.1064 | -59929.0183 | -20120.7151 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09
|  |  | ADIT (e.o.y.) | 0 | -14474.1611 | -72432.8376 | -170349.8345 | -304968.7601 | -473259.3365 | -672422.3736 | -899853.4989 | -1153147.4429 | -1432376.9305 | -1738104.2728 | -2052927.7442 | -2341372.0218 | -2608437.7077 | -2858787.0448 | -3096831.2463 | -3326691.8896 | -3552279.0366 | -3777253.4962 | -4002226.9614 | -4227201.421 | -4433722.3985 | -4602941.7113 | -4734028.4411 | -4826153.9527 | -4878450.8178 | -4890053.0876 | -4860055.1995 | -4787552.2317 | -4671598.7907 | -4511249.2477 | -4328455.0471 | -4145660.8466 | -3962866.646 | -3780072.4454 | -3597278.2448 | -3414484.0442 | -3231689.8436 | -3048895.643 | -2866101.4424 | -2683307.2418 | -2500513.0412 | -2317718.8406 | -2134924.64 | -1952130.4394 | -1769336.2388 | -1586542.0382 | -1403747.8376 | -1220953.637 | -1038159.4364 | -855365.2358 | -689112.9336 | -539766.4516 | -407697.7178 | -293286.8427 | -196922.2991 | -119001.1064 | -59929.0183 | -20120.7151 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09
|  |  | Net Rate Base | 0 | 2947206.2574 | 5870745.2061 | 8757991.6309 | 11612456.2609 | 14437404.4942 | 17235875.8134 | 20010699.4929 | 22764510.6517 | 25498608.7266 | 28212812.2937 | 27242987.1824 | 26281803.6034 | 25344498.9172 | 24426241.7012 | 23522495.2275 | 22628993.1006 | 21741719.5009 | 20856888.9932 | 19972365.3263 | 19087841.6594 | 18212544.2364 | 17365124.3868 | 16555421.661 | 15784265.8358 | 15052504.943 | 14361005.6711 | 13710653.7757 | 13102354.4992 | 12537032.9992 | 12015634.7867 | 11527656.9539 | 11050901.4501 | 10574145.9462 | 10097390.4423 | 9620634.9384 | 9143879.4345 | 8667123.9306 | 8190368.4268 | 7713612.9229 | 7236857.419 | 6760101.9151 | 6283346.4112 | 5806590.9074 | 5329835.4035 | 4853079.8996 | 4376324.3957 | 3899568.8918 | 3422813.388 | 2946057.8841 | 2469302.3802 | 2014118.7891 | 1602553.6057 | 1235566.4349 | 914137.9931 | 639270.5722 | 411988.5147 | 233338.6987 | 104391.0334 | 26238.9661 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09 | -1.1569e-09
|  |  | Pre-Tax return on rate base | 0 | 263185.5188 | 524257.5469 | 782088.6526 | 1036992.3441 | 1289260.2213 | 1539163.7101 | 1786955.4647 | 2032870.8012 | 2277025.7593 | 2519404.1378 | 2432798.7554 | 2346965.0618 | 2263263.7533 | 2181263.3839 | 2100558.8238 | 2020769.0839 | 1941535.5514 | 1862520.1871 | 1783532.2236 | 1704544.2602 | 1626380.2003 | 1550705.6077 | 1478399.1543 | 1409534.9391 | 1344188.6914 | 1282437.8064 | 1224361.3822 | 1170040.2568 | 1119557.0468 | 1072996.1864 | 1029419.766 | 986845.4995 | 944271.233 | 901696.9665 | 859122.7 | 816548.4335 | 773974.167 | 731399.9005 | 688825.634 | 646251.3675 | 603677.101 | 561102.8345 | 518528.568 | 475954.3015 | 433380.035 | 390805.7685 | 348231.502 | 305657.2355 | 263082.969 | 220508.7026 | 179860.8079 | 143108.037 | 110336.0826 | 81632.5228 | 57086.8621 | 36790.5744 | 20837.1458 | 9322.1193 | 2343.1397 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10 | -1.0331e-10

## Baseline scaling factors
Mitigation Scenario - line miles UG/OH
Project Type - Phase | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
OH-1PH | 19.95 | 19.95 | 19.95 | 19.95 | 19.95 | 19.95 | 19.95 | 19.95 | 19.95 | 19.95
OH-3PH | 51.32 | 51.32 | 51.32 | 51.32 | 51.32 | 51.32 | 51.32 | 51.32 | 51.32 | 51.32
UG-1PH | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6
| 120.87 | 120.87 | 120.87 | 120.87 | 120.87 | 120.87 | 120.87 | 120.87 | 120.87 | 120.87
Total storm restoration cost (OH remaining at risk*avg storm per mile escalated)+((Mitigation at baseline pace*avg storm cost per mile escalated*(1-effectiveness))
Baseline Scenario
Project Type - Phase | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
OH-1PH | 48666.9287 | 48421.8903 | 47509.9874 | 45979.7617 | 43876.7722 | 41243.7632 | 38120.8243 | 34545.5412 | 30553.1387 | 26176.6155
OH-3PH | 125192.3199 | 124561.9754 | 122216.168 | 118279.7681 | 112869.9724 | 106096.7382 | 98063.1931 | 88866.0238 | 78595.8435 | 67337.5392
UG-1PH | 119932.7692 | 118101.0443 | 114463.9756 | 109152.9759 | 102291.3827 | 93994.9141 | 84372.1011 | 73524.6965 | 61548.0608 | 48531.5288
Mitigation Scenario
Project Type - Phase | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
OH-1PH | 5348.0141 | 5876.6883 | 6405.3625 | 6934.0367 | 7462.7109 | 7991.3851 | 8520.0592 | 9048.7334 | 9577.4076 | 10106.0818
OH-3PH | 13757.3978 | 15117.3757 | 16477.3536 | 17837.3315 | 19197.3094 | 20557.2873 | 21917.2652 | 23277.2431 | 24637.221 | 25997.1989
UG-1PH | 2659.2632 | 2922.1428 | 3185.0224 | 3447.902 | 3710.7816 | 3973.6611 | 4236.5407 | 4499.4203 | 4762.2999 | 5025.1795
Escalate the costs per mile with Handy-Whitman 10-yr average for North Atlantic Distribution Plant costs. This reduces the amount of miles treated with the baseline spending
Project Type - Phase | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
OH-1PH | 502821.604 | 537570.2227 | 574720.2229 | 614437.5574 | 656899.6478 | 702296.1765 | 750829.9345 | 802717.7271 | 858191.3423 | 917498.5866
OH-3PH | 703872.233 | 752514.908 | 804519.1444 | 860117.2507 | 919557.5892 | 983105.6862 | 1051045.4173 | 1123680.2766 | 1201334.7312 | 1284355.6718
UG-1PH | 601670.6048 | 643250.4062 | 687703.6733 | 735228.9836 | 786038.6373 | 840359.6065 | 898434.5486 | 960522.8902 | 1026901.9865 | 1097868.3596
Baseline annual CAPEX investment adjusted for inflation
Project Type - Phase | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
OH-1PH | 1003129.1 | 1025197.9402 | 1047752.2949 | 1070802.8454 | 1094360.508 | 1118436.4391 | 1143042.0408 | 1168188.9657 | 1193889.1229 | 1220154.6837
OH-3PH | 3612272.3 | 3691742.2906 | 3772960.621 | 3855965.7547 | 3940797.0013 | 4027494.5353 | 4116099.4151 | 4206653.6022 | 4299199.9814 | 4393782.381
UG-1PH | 2984286.2 | 3049940.4964 | 3117039.1873 | 3185614.0494 | 3255697.5585 | 3327322.9048 | 3400524.0087 | 3475335.5369 | 3551792.9187 | 3629932.3629
Determine the number of cumulative line miles treated in each baseline year, assuming a fixed CAPEX budget
Project Type - Phase | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | QAQC sumcheck
OH-1PH | 1.995 | 3.9021 | 5.7252 | 7.4679 | 9.1338 | 10.7264 | 12.2488 | 13.7041 | 15.0952 | 16.4251
OH-3PH | 5.132 | 10.0379 | 14.7276 | 19.2107 | 23.4962 | 27.5929 | 31.5091 | 35.2527 | 38.8314 | 42.2524
UG-1PH | 4.96 | 9.7015 | 14.234 | 18.5668 | 22.7087 | 26.6681 | 30.4531 | 34.0712 | 37.53 | 40.8363
Total Annual Inc. Miles | 12.087 | 23.6414 | 34.6867 | 45.2454 | 55.3387 | 64.9874 | 74.2109 | 83.028 | 91.4566 | 99.5138 | 82.33% | so this means 82% of the accelerated case miles treated in the baseline scenario
Remaining at Risk (defined as the number of line miles left untreated in the baseline scenario by year compared to the mitigation case.)
Project Type - Phase | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
OH-1PH | 17.955 | 16.0479 | 14.2248 | 12.4821 | 10.8162 | 9.2236 | 7.7012 | 6.2459 | 4.8548 | 3.5249
OH-3PH | 46.188 | 41.2821 | 36.5924 | 32.1093 | 27.8238 | 23.7271 | 19.8109 | 16.0673 | 12.4886 | 9.0676
UG-1PH | 44.64 | 39.8985 | 35.366 | 31.0332 | 26.8913 | 22.9319 | 19.1469 | 15.5288 | 12.07 | 8.7637
Total Annual Inc. Miles | 108.783 | 97.2286 | 86.1833 | 75.6246 | 65.5313 | 55.8826 | 46.6591 | 37.842 | 29.4134 | 21.3562 | 0 | <<should equal zero because this totals the baseline treated cumulative miles and left at risk, compared to the accelerated case treated miles
Reliability ramping factors - defined as the percentage of the miles either mitigated or left at risk in the Baseline Scenario
Baseline Mitigated percent
Project Type - Phase | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
OH-1PH | 10% | 19.56% | 28.7% | 37.43% | 45.78% | 53.77% | 61.4% | 68.69% | 75.67% | 82.33%
OH-3PH | 10% | 19.56% | 28.7% | 37.43% | 45.78% | 53.77% | 61.4% | 68.69% | 75.67% | 82.33%
UG-1PH | 10% | 19.56% | 28.7% | 37.43% | 45.78% | 53.77% | 61.4% | 68.69% | 75.67% | 82.33%
Baseline Remaining At Risk percent
Project Type - Phase | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
OH-1PH | 90% | 80.44% | 71.3% | 62.57% | 54.22% | 46.23% | 38.6% | 31.31% | 24.33% | 17.67%
OH-3PH | 90% | 80.44% | 71.3% | 62.57% | 54.22% | 46.23% | 38.6% | 31.31% | 24.33% | 17.67%
UG-1PH | 90% | 80.44% | 71.3% | 62.57% | 54.22% | 46.23% | 38.6% | 31.31% | 24.33% | 17.67%
QAQC check | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Baseline non-storm related costs
Project Type - Phase | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
OH-1PH | 7329.9045 | 6783.8427 | 6261.8415 | 5762.8409 | 5285.8274 | 4829.8321 | 4393.9291 | 3977.2328 | 3578.8972 | 3198.1131 | OH | 1PH
OH-3PH | 82617.4965 | 76462.6738 | 70579.0463 | 64954.6646 | 59578.1057 | 54438.4499 | 49525.2589 | 44828.554 | 40338.7965 | 36046.8676 | OH | 3PH
UG-1PH | 22138.118 | 20255.5027 | 18455.8397 | 16735.4738 | 15090.9111 | 13518.8115 | 12015.9821 | 10579.3708 | 9206.0597 | 7893.2598 | UG | 1PH
Total | 112085.5189 | 103502.0192 | 95296.7275 | 87452.9793 | 79954.8442 | 72787.0936 | 65935.1701 | 59385.1577 | 53123.7534 | 47138.2405
Mitigation Case non-storm related costs
Project Type - Phase | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
OH-1PH | 2188.8203 | 2188.8203 | 2188.8203 | 2188.8203 | 2188.8203 | 2188.8203 | 2188.8203 | 2188.8203 | 2188.8203 | 2188.8203 | OH | 1PH
OH-3PH | 24670.833 | 24670.833 | 24670.833 | 24670.833 | 24670.833 | 24670.833 | 24670.833 | 24670.833 | 24670.833 | 24670.833 | OH | 3PH
UG-1PH | 4413.5988 | 4413.5988 | 4413.5988 | 4413.5988 | 4413.5988 | 4413.5988 | 4413.5988 | 4413.5988 | 4413.5988 | 4413.5988 | UG | 1PH
Total | 31273.252 | 31273.252 | 31273.252 | 31273.252 | 31273.252 | 31273.252 | 31273.252 | 31273.252 | 31273.252 | 31273.252

## Baseline Projects
[16 empty] | RES CUSTOMER CONSEQUENCES (#Outage Events) - BASELINE - RAMPED | [9 empty] | NONRES CUSTOMER CONSEQUENCES (#Outage Events) - BASELINE - RAMPED | [9 empty] | RES RISK VALUE - MONETIZED - TOTAL $ USING ICE CALCULATOR WEIGHTED AVERAGE $/event | [9 empty] | NONRES RISK VALUE - MONETIZED - TOTAL $ USING ICE CALCULATOR WEIGHTED AVERAGE $/event | [9 empty] | TOTAL CIRCUIT CUSTOMER RISK VALUE - MONETIZED - TOTAL $ USING ICE CALCULATOR WEIGHTED AVERAGE $/event | [9 empty] | Total non-storm costs | [20 empty] | Feeder backup value - Res | [9 empty] | Feeder backup value - NonRes
Baseline Reliability calculations - Rolling Baseline Improvements | [10 empty] | Percent of customers by class |  |  |  |  | Year | [9 empty] | Year | [9 empty] | Year | [9 empty] | Year | [9 empty] | Year | [10 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Circuit | District | Project | Name | Start Tag | Protective device | Phase | OH/UG | Zone | Customers on project | Construction Cost Estimate (fully loaded) | RES % | NONRES % | Percent of Customers Impacted by Mitigation | Effectiveness Score | Applicability Score | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | Number of non-storm Incidents (pre-mitigation) (per Zone) | Times the Customers Impacted by Mitigation factor and multi-project weighting | [9 empty] | Restoration Cost - Pre
CV-G65 | Springfield | 175351 | 175351: Cavendish line 2 | 520170 | Sub Breaker | 3PH | OH | Zone 1 | 331 | 91748.4 | 89.64% | 10.36% | 100% | 90% | 80.33% | 570.8294 | 528.3039 | 487.6521 | 448.7916 | 411.6433 | 376.1318 | 342.1851 | 309.7341 | 278.713 | 249.0588 | 65.9374 | 61.0252 | 56.3295 | 51.8406 | 47.5496 | 43.4476 | 39.5263 | 35.7779 | 32.1946 | 28.7692 | 11987.4184 | 11094.382 | 10240.6947 | 9424.6228 | 8644.5089 | 7898.7685 | 7185.8871 | 6504.4168 | 5852.9737 | 5230.2346 | 256166.7803 | 237082.9158 | 218839.9289 | 201400.7687 | 184730.0168 | 168793.8154 | 153559.7986 | 138997.0266 | 125075.9229 | 111768.214 | 268154.1988 | 248177.2978 | 229080.6236 | 210825.3915 | 193374.5257 | 176692.5839 | 160745.6858 | 145501.4435 | 130928.8965 | 116998.4485 | 3.2948 | 2.0074 | 1.8579 | 1.7149 | 1.5783 | 1.4476 | 1.3227 | 1.2034 | 1.0892 | 0.98014 | 0.87586 | 947.5027 | 876.9158 | 809.4392 | 744.9357 | 683.2744 | 624.33 | 567.9828 | 514.1184 | 462.6274 | 413.4052 | 2689.777 | 5261.0364 | 7719.0003 | 10068.6609 | 12314.7902 | 14461.9501 | 16514.5013 | 18476.6125 | 20352.2687 | 22145.2793 | 57479.5574 | 112426.4373 | 164952.235 | 215163.629 | 263162.5968 | 309046.6231 | 352908.8968 | 394838.5008 | 434920.593 | 473236.5787
EL-G40 | White River Jct | 197817 | 197817: ELY-129 G40 Zone 1 LC | 620436 | 0 | 3PH | OH | Zone 2 | 1015 | 178201.2 | 85.29% | 14.71% | 100% | 90% | 80.33% | 1029.8107 | 953.0921 | 879.7538 | 809.647 | 742.6293 | 678.5645 | 617.3225 | 558.779 | 502.8151 | 449.3171 | 177.5947 | 164.3643 | 151.7168 | 139.6266 | 128.0692 | 117.021 | 106.4596 | 96.3635 | 86.7123 | 77.4864 | 21626.0252 | 20014.9337 | 18474.8304 | 17002.5875 | 15595.215 | 14249.8544 | 12963.7734 | 11734.3599 | 10559.1172 | 9435.6583 | 689955.3077 | 638555.1472 | 589419.7924 | 542449.4509 | 497548.7275 | 454626.4302 | 413595.385 | 374372.2592 | 336877.3919 | 301034.6321 | 711581.333 | 658570.0809 | 607894.6228 | 559452.0385 | 513143.9425 | 468876.2845 | 426559.1584 | 386106.6192 | 347436.5091 | 310470.2904 | 11.0221 | 4.5721 | 4.2315 | 3.9059 | 3.5946 | 3.2971 | 3.0126 | 2.7407 | 2.4808 | 2.2324 | 1.9948 | 2158.0222 | 1997.2543 | 1843.5702 | 1696.6577 | 1556.2185 | 1421.9674 | 1293.6317 | 1170.9507 | 1053.6753 | 941.5674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DM-G6 | Brattleboro | 199297 | 199297: L66 P15-1 to L62 P140 | 554333 | 554331 | 3PH | OH | Zone 2 | 254 | 245623.4 | 89.45% | 10.55% | 100% | 90% | 80.33% | 707.5637 | 654.8518 | 604.4624 | 556.2934 | 510.2467 | 466.229 | 424.1508 | 383.9266 | 345.4749 | 308.7174 | 83.4859 | 77.2664 | 71.3209 | 65.6374 | 60.2043 | 55.0107 | 50.0458 | 45.2998 | 40.7628 | 36.4258 | 14858.8382 | 13751.8872 | 12693.711 | 11682.1604 | 10715.181 | 9790.8089 | 8907.1666 | 8062.4596 | 7254.9723 | 6483.0647 | 324342.7467 | 300179.9218 | 277081.7649 | 255001.3644 | 233893.8755 | 213716.4298 | 194428.0473 | 175989.5539 | 158363.5017 | 141514.0927 | 339201.5848 | 313931.8091 | 289775.476 | 266683.5248 | 244609.0566 | 223507.2386 | 203335.2139 | 184052.0135 | 165618.474 | 147997.1574 | 56.6756 | 23.4295 | 21.6841 | 20.0156 | 18.4205 | 16.8958 | 15.4382 | 14.0449 | 12.713 | 11.4397 | 10.2226 | 11058.7465 | 10234.8941 | 9447.3425 | 8694.4921 | 7974.814 | 7286.8466 | 6629.1925 | 6000.5161 | 5399.5406 | 4825.0454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SH-G35 | Royalton | 199309 | 199309: Fay Brook Rd. | 599580 | 476994 | 1PH | UG | Zone 3 | 210 | 69431.1 | 86.72% | 13.28% | 50% | 98% | 83.36% | 387.6035 | 354.6419 | 323.1326 | 293.0117 | 264.218 | 236.6931 | 210.3809 | 185.2281 | 161.1836 | 138.1985 | 59.3627 | 54.3145 | 49.4888 | 44.8757 | 40.4658 | 36.2503 | 32.2205 | 28.3683 | 24.6858 | 21.1655 | 8139.6736 | 7447.4795 | 6785.7851 | 6153.2464 | 5548.5787 | 4970.5541 | 4417.9985 | 3889.7898 | 3384.8551 | 2902.1689 | 230624.0839 | 211011.9191 | 192263.91 | 174341.98 | 157209.7303 | 140832.3656 | 125176.6243 | 110210.7098 | 95904.2269 | 82228.1195 | 238763.7575 | 218459.3986 | 199049.6951 | 180495.2264 | 162758.309 | 145802.9197 | 129594.6228 | 114100.4995 | 99289.0819 | 85130.2884 | 25.1076 | 4.9007 | 4.4839 | 4.0855 | 3.7047 | 3.3406 | 2.9926 | 2.66 | 2.3419 | 2.0379 | 1.7473 | 2313.1173 | 2116.4109 | 1928.3718 | 1748.6181 | 1576.7848 | 1412.5228 | 1255.4986 | 1105.3932 | 961.9018 | 824.733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SH-G35 | Royalton | 199373 | 199373: FAY BROOK RD P.44 -P.75 | 617377 | 476994 | 1PH | UG | Zone 3 | 135 | 86792.1 | 86.72% | 13.28% | 50% | 98% | 83.36% | 249.1737 | 227.9841 | 207.7281 | 188.3647 | 169.8545 | 152.1598 | 135.2449 | 119.0752 | 103.618 | 88.8419 | 38.1617 | 34.9165 | 31.8142 | 28.8486 | 26.0137 | 23.3038 | 20.7132 | 18.2367 | 15.8694 | 13.6064 | 5232.6473 | 4787.6654 | 4362.2904 | 3955.6584 | 3566.9435 | 3195.3562 | 2840.1419 | 2500.5791 | 2175.9783 | 1865.68 | 148258.3397 | 135650.5194 | 123598.2279 | 112076.9872 | 101063.398 | 90535.0922 | 80470.687 | 70849.742 | 61652.7173 | 52860.934 | 153490.987 | 140438.1848 | 127960.5183 | 116032.6455 | 104630.3415 | 93730.4484 | 83310.8289 | 73350.3211 | 63828.6955 | 54726.614 | 25.1076 | 3.1504 | 2.8825 | 2.6264 | 2.3816 | 2.1476 | 1.9238 | 1.71 | 1.5055 | 1.3101 | 1.1233 | 1487.004 | 1360.5499 | 1239.6676 | 1124.1117 | 1013.6474 | 908.0504 | 807.1063 | 710.6099 | 618.3655 | 530.1855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EL-G40 | White River Jct | 199494 | 199494: L3P52 | 619216 | 620436 | 3PH | OH | Zone 2 | 840 | 222700.5 | 85.29% | 14.71% | 100% | 90% | 80.33% | 852.2572 | 788.7659 | 728.0721 | 670.0527 | 614.5898 | 561.5706 | 510.8876 | 462.4378 | 416.1228 | 371.8486 | 146.9749 | 136.0256 | 125.5587 | 115.5531 | 105.9883 | 96.8449 | 88.1045 | 79.7491 | 71.7619 | 64.1267 | 17897.4002 | 16564.0831 | 15289.5148 | 14071.1069 | 12906.3848 | 11792.9829 | 10728.64 | 9711.1944 | 8738.5798 | 7808.8207 | 570997.4961 | 528459.4322 | 487795.6902 | 448923.6835 | 411764.4642 | 376242.5629 | 342285.8359 | 309825.318 | 278795.083 | 249132.1093 | 588894.8963 | 545023.5152 | 503085.2051 | 462994.7905 | 424670.849 | 388035.5458 | 353014.4759 | 319536.5124 | 287533.6627 | 256940.93 | 11.0221 | 3.7838 | 3.5019 | 3.2324 | 2.9749 | 2.7286 | 2.4932 | 2.2682 | 2.0531 | 1.8475 | 1.6509 | 1785.9494 | 1652.9001 | 1525.7132 | 1404.1305 | 1287.905 | 1176.8006 | 1070.5917 | 969.0627 | 872.0072 | 779.2282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SH-G35 | Royalton | 199498 | 199498: Brk Rd. P.75-L.81P.76 | 617059 | 476994, 618154 | 1PH | UG | Zone 3 | 107 | 173545.2 | 86.72% | 13.28% | 50% | 98% | 83.36% | 197.4932 | 180.6985 | 164.6438 | 149.2965 | 134.6254 | 120.6007 | 107.1941 | 94.3781 | 82.1269 | 70.4154 | 30.2467 | 27.6745 | 25.2157 | 22.8652 | 20.6183 | 18.4704 | 16.4171 | 14.4543 | 12.578 | 10.7843 | 4147.3575 | 3794.6681 | 3457.5191 | 3135.2255 | 2827.133 | 2532.6157 | 2251.0754 | 1981.9405 | 1724.6642 | 1478.7242 | 117508.4618 | 107515.5969 | 97963.0399 | 88831.3898 | 80102.1007 | 71757.4434 | 63780.4705 | 56154.9807 | 48865.487 | 41897.1847 | 121655.8193 | 111310.265 | 101420.5589 | 91966.6153 | 82929.2336 | 74290.0591 | 66031.5459 | 58136.9212 | 50590.1513 | 43375.9089 | 25.1076 | 2.497 | 2.2847 | 2.0817 | 1.8876 | 1.7021 | 1.5248 | 1.3553 | 1.1933 | 1.0384 | 0.8903 | 1178.5884 | 1078.3617 | 982.5513 | 890.9626 | 803.4094 | 719.714 | 639.7064 | 563.2242 | 490.1119 | 420.2211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SH-G35 | Royalton | 199569 | 199569: Brook Rd. P.76 to 50X | 618225 | 618154 | 1PH | UG | Zone 3 | 42 | 97852.8 | 86.72% | 13.28% | 50% | 98% | 83.36% | 77.5207 | 70.9284 | 64.6265 | 58.6023 | 52.8436 | 47.3386 | 42.0762 | 37.0456 | 32.2367 | 27.6397 | 11.8725 | 10.8629 | 9.8978 | 8.9751 | 8.0932 | 7.2501 | 6.4441 | 5.6737 | 4.9372 | 4.2331 | 1627.9347 | 1489.4959 | 1357.157 | 1230.6493 | 1109.7157 | 994.1108 | 883.5997 | 777.958 | 676.971 | 580.4338 | 46124.8168 | 42202.3838 | 38452.782 | 34868.396 | 31441.9461 | 28166.4731 | 25035.3249 | 22042.142 | 19180.8454 | 16445.6239 | 47752.7515 | 43691.8797 | 39809.939 | 36099.0453 | 32551.6618 | 29160.5839 | 25918.9246 | 22820.0999 | 19857.8164 | 17026.0577 | 25.1076 | 0.98013 | 0.89678 | 0.81711 | 0.74094 | 0.66813 | 0.59853 | 0.53199 | 0.46839 | 0.40759 | 0.34946 | 462.6235 | 423.2822 | 385.6744 | 349.7236 | 315.357 | 282.5046 | 251.0997 | 221.0786 | 192.3804 | 164.9466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DM-G6 | Brattleboro | 199616 | 199616: Newfane L66 P1-105 | 556104 | 0 | 1PH | OH | Zone 3 | 363 | 125865.3 | 89.45% | 10.55% | 50% | 90% | 80.33% | 508.9416 | 471.0266 | 434.7822 | 400.1348 | 367.014 | 335.3526 | 305.0863 | 276.1536 | 248.4957 | 222.0565 | 60.0504 | 55.5767 | 51.3002 | 47.2122 | 43.3042 | 39.5685 | 35.9973 | 32.5835 | 29.3202 | 26.2006 | 10687.7745 | 9891.5587 | 9130.426 | 8402.8304 | 7707.2943 | 7042.4051 | 6406.8124 | 5799.2253 | 5218.4099 | 4663.1865 | 233295.6394 | 215915.6248 | 199301.4124 | 183419.2593 | 168236.9093 | 153723.5275 | 139849.6377 | 126587.0624 | 113908.8658 | 101789.2988 | 243983.414 | 225807.1836 | 208431.8384 | 191822.0897 | 175944.2036 | 160765.9326 | 146256.4501 | 132386.2878 | 119127.2757 | 106452.4853 | 39.4003 | 5.4289 | 5.0245 | 4.6379 | 4.2683 | 3.915 | 3.5772 | 3.2544 | 2.9458 | 2.6507 | 2.3687 | 2562.453 | 2371.5558 | 2189.0701 | 2014.625 | 1847.8664 | 1688.4555 | 1536.0687 | 1390.3963 | 1251.1426 | 1118.0247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DM-G6 | Brattleboro | 199621 | 199621: Brookline L62 P140-195 | 472083 | 0 | 1PH | OH | Zone 3 | 43 | 238522.4 | 89.45% | 10.55% | 50% | 90% | 80.33% | 60.2879 | 55.7965 | 51.5031 | 47.3989 | 43.4755 | 39.725 | 36.1397 | 32.7124 | 29.4361 | 26.3042 | 7.1134 | 6.5835 | 6.0769 | 5.5926 | 5.1297 | 4.6872 | 4.2641 | 3.8598 | 3.4732 | 3.1037 | 1266.0449 | 1171.7273 | 1081.5656 | 995.3766 | 912.9853 | 834.2243 | 758.9337 | 686.9606 | 618.1587 | 552.3885 | 27635.5716 | 25576.782 | 23608.7073 | 21727.3503 | 19928.8901 | 18209.6741 | 16566.2105 | 14995.1617 | 13493.3367 | 12057.6855 | 28901.6165 | 26748.5093 | 24690.2729 | 22722.7269 | 20841.8754 | 19043.8984 | 17325.1442 | 15682.1222 | 14111.4955 | 12610.074 | 39.4003 | 0.6431 | 0.59519 | 0.54939 | 0.50561 | 0.46376 | 0.42375 | 0.38551 | 0.34895 | 0.314 | 0.28059 | 303.5413 | 280.9281 | 259.3113 | 238.647 | 218.8933 | 200.0099 | 181.9585 | 164.7026 | 148.207 | 132.4382 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BV-G44 | Springfield | 199623 | 199623: BV Sub to L4 P126 | Sub breaker | 0 | 3PH | OH | Zone 1 | 797 | 110990.3 | 85.77% | 14.23% | 100% | 90% | 80.33% | 1515.8773 | 1402.9478 | 1294.9942 | 1191.7972 | 1093.1474 | 998.8443 | 908.6964 | 822.5206 | 740.1419 | 661.393 | 251.5332 | 232.7946 | 214.8816 | 197.7578 | 181.3886 | 165.7407 | 150.7822 | 136.4829 | 122.8136 | 109.7466 | 31833.4243 | 29461.9038 | 27194.8779 | 25027.7421 | 22956.0952 | 20975.7297 | 19082.6235 | 17272.9318 | 15542.9791 | 13889.252 | 977206.6587 | 904406.9011 | 834814.8632 | 768289.2059 | 704694.8173 | 643902.5395 | 585788.905 | 530235.887 | 477130.6588 | 426365.3655 | 1009040.083 | 933868.8049 | 862009.7411 | 793316.948 | 727650.9126 | 664878.2692 | 604871.5285 | 547508.8187 | 492673.6379 | 440254.6175 | 24.3714 | 14.532 | 13.4494 | 12.4145 | 11.4252 | 10.4795 | 9.5755 | 8.7113 | 7.8851 | 7.0954 | 6.3405 | 6859.1152 | 6348.1262 | 5859.6524 | 5392.7019 | 4946.3263 | 4519.6189 | 4111.7133 | 3721.7809 | 3349.0297 | 2992.7029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BV-G44 | Springfield | 199973 | 199973: L41 VT Route 106 - Spacer | 526376 | 0 | 3PH | OH | Zone 1 | 197 | 155353.3 | 85.77% | 14.23% | 100% | 90% | 80.33% | 374.6899 | 346.7763 | 320.0927 | 294.5848 | 270.2008 | 246.8912 | 224.6088 | 203.3081 | 182.946 | 163.4811 | 62.1732 | 57.5414 | 53.1138 | 48.8812 | 44.8351 | 40.9673 | 37.2699 | 33.7354 | 30.3567 | 27.1268 | 7868.4876 | 7282.3025 | 6721.946 | 6186.28 | 5674.2168 | 5184.7161 | 4716.784 | 4269.47 | 3841.8656 | 3433.1024 | 241542.9257 | 223548.5063 | 206346.9612 | 189903.3545 | 174184.2899 | 159157.8423 | 144793.4935 | 131062.0699 | 117935.6835 | 105387.675 | 249411.4132 | 230830.8087 | 213068.9072 | 196089.6346 | 179858.5066 | 164342.5584 | 149510.2774 | 135331.5399 | 121777.5491 | 108820.7775 | 24.3714 | 3.592 | 3.3244 | 3.0686 | 2.824 | 2.5903 | 2.3668 | 2.1532 | 1.949 | 1.7538 | 1.5672 | 1695.4149 | 1569.1102 | 1448.3708 | 1332.9514 | 1222.6177 | 1117.1455 | 1016.3206 | 919.9383 | 827.8028 | 739.7271 | 163.1727 | 319.1556 | 468.2656 | 610.8054 | 747.0647 | 877.32 | 1001.836 | 1120.8656 | 1234.6504 | 1343.4216 | 5008.994 | 9797.2805 | 14374.5844 | 18750.2021 | 22933.0203 | 26931.5342 | 30753.8647 | 34407.7748 | 37900.6854 | 41239.6906
CV-G65 | Springfield | 201142 | 201142: L208 HIGH ST. - CIC |  |  | 1PH | UG | Zone 3 | 122 | 107650.3 | 89.64% | 10.36% | 50% | 98% | 83.36% | 135.6334 | 124.0992 | 113.0732 | 102.5331 | 92.4574 | 82.8256 | 73.6182 | 64.8165 | 56.4027 | 48.3596 | 15.6672 | 14.3349 | 13.0613 | 11.8438 | 10.6799 | 9.5673 | 8.5038 | 7.4871 | 6.5152 | 5.5861 | 2848.3021 | 2606.0838 | 2374.5382 | 2153.195 | 1941.6047 | 1739.3375 | 1545.9827 | 1361.1475 | 1184.4566 | 1015.551 | 60867.1821 | 55691.0652 | 50743.0196 | 46012.996 | 41491.3877 | 37169.0116 | 33037.089 | 29087.2281 | 25311.4069 | 21701.9569 | 63715.4842 | 58297.1491 | 53117.5579 | 48166.191 | 43432.9924 | 38908.3491 | 34583.0717 | 30448.3756 | 26495.8635 | 22717.5079 | 7.0795 | 2.2032 | 2.0158 | 1.8367 | 1.6655 | 1.5018 | 1.3454 | 1.1958 | 1.0529 | 0.91619 | 0.78554 | 1039.9041 | 951.4711 | 866.9347 | 786.1232 | 708.8724 | 635.0254 | 564.4323 | 496.9497 | 432.4405 | 370.7738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DM-G6 | Brattleboro | 201143 | 201143: L61 DOVER RD. - CIC | 498311 | 0 | 1PH | UG | Zone 3 | 170 | 245801.3 | 89.45% | 10.55% | 50% | 98% | 83.36% | 235.9336 | 215.87 | 196.6903 | 178.3558 | 160.8291 | 144.0747 | 128.0585 | 112.748 | 98.1122 | 84.1212 | 27.838 | 25.4706 | 23.2076 | 21.0443 | 18.9763 | 16.9995 | 15.1097 | 13.3032 | 11.5763 | 9.9255 | 4954.6065 | 4533.269 | 4130.4967 | 3745.4714 | 3377.4111 | 3025.5684 | 2689.2287 | 2367.7089 | 2060.3559 | 1766.5457 | 108150.4929 | 98953.4253 | 90161.601 | 81757.1641 | 73723.0455 | 66042.928 | 58701.2136 | 51682.9916 | 44974.0081 | 38560.6373 | 113105.0994 | 103486.6944 | 94292.0977 | 85502.6355 | 77100.4566 | 69068.4964 | 61390.4424 | 54050.7005 | 47034.364 | 40327.183 | 39.4003 | 2.5167 | 2.3027 | 2.0981 | 1.9025 | 1.7156 | 1.5369 | 1.366 | 1.2027 | 1.0466 | 0.89733 | 1187.8943 | 1086.8763 | 990.3094 | 897.9974 | 809.753 | 725.3967 | 644.7574 | 567.6713 | 493.9817 | 423.5391 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DM-G6 | Brattleboro | 201149 | 201149: L6 VT RT 30 - CIC | 476653 | 0 | 1PH | UG | Zone 3 | 194 | 251576.7 | 89.45% | 10.55% | 50% | 98% | 83.36% | 269.2419 | 246.3457 | 224.4584 | 203.5354 | 183.5344 | 164.4146 | 146.1374 | 128.6654 | 111.9633 | 95.9972 | 31.768 | 29.0665 | 26.484 | 24.0153 | 21.6553 | 19.3994 | 17.2428 | 15.1813 | 13.2106 | 11.3268 | 5654.0803 | 5173.26 | 4713.6256 | 4274.2438 | 3854.2221 | 3452.7075 | 3068.8846 | 2701.9737 | 2351.2297 | 2015.9403 | 123418.7978 | 112923.3207 | 102890.2976 | 93299.352 | 84131.0048 | 75366.6355 | 66988.4438 | 58979.4139 | 51323.2798 | 44004.492 | 129072.8782 | 118096.5806 | 107603.9233 | 97573.5958 | 87985.2269 | 78819.343 | 70057.3283 | 61681.3876 | 53674.5095 | 46020.4323 | 39.4003 | 2.872 | 2.6278 | 2.3943 | 2.1711 | 1.9578 | 1.7538 | 1.5589 | 1.3725 | 1.1943 | 1.024 | 1355.597 | 1240.3176 | 1130.1178 | 1024.7736 | 924.071 | 827.8057 | 735.782 | 647.8131 | 563.7203 | 483.3328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CH-G11 | Springfield | 201152 | 201152: L342 TOWNSHEND RD | 488351 | 0 | 1PH | OH | Zone 3 | 73 | 261770.4 | 85.9% | 14.1% | 50% | 90% | 80.33% | 303.1388 | 280.5557 | 258.9675 | 238.3307 | 218.6031 | 199.7447 | 181.7173 | 164.4842 | 148.0105 | 132.2626 | 49.7638 | 46.0565 | 42.5126 | 39.1248 | 35.8863 | 32.7905 | 29.8311 | 27.002 | 24.2977 | 21.7125 | 6365.9156 | 5891.6689 | 5438.3184 | 5004.9437 | 4590.6643 | 4194.6391 | 3816.0636 | 3454.169 | 3108.2202 | 2777.5148 | 193332.4899 | 178929.6425 | 165161.4167 | 151999.8496 | 139418.2105 | 127390.9466 | 115893.6307 | 104902.9122 | 94396.4692 | 84352.9636 | 199698.4056 | 184821.3114 | 170599.7351 | 157004.7933 | 144008.8749 | 131585.5856 | 119709.6942 | 108357.0811 | 97504.6895 | 87130.4784 | 20.331 | 4.6203 | 4.2761 | 3.9471 | 3.6326 | 3.3319 | 3.0444 | 2.7697 | 2.507 | 2.2559 | 2.0159 | 2180.7983 | 2018.3336 | 1863.0274 | 1714.5644 | 1572.643 | 1436.975 | 1307.2848 | 1183.3091 | 1064.796 | 951.5048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BV-G43 | Springfield | 201153 | 201153: L438 BROWNSVILLE - CIC | 0 | 0 | 1PH | UG | Zone 3 | 165 | 144234.5 | 87.31% | 12.69% | 50% | 98% | 83.36% | 180.5366 | 165.1839 | 150.5076 | 136.478 | 123.0666 | 110.2461 | 97.9905 | 86.2749 | 75.0755 | 64.3696 | 26.2441 | 24.0124 | 21.8789 | 19.8395 | 17.8899 | 16.0262 | 14.2446 | 12.5416 | 10.9135 | 9.3572 | 3791.2694 | 3468.8616 | 3160.6598 | 2866.0381 | 2584.3981 | 2315.1677 | 2057.8003 | 1811.773 | 1576.5862 | 1351.7623 | 101958.4985 | 93287.9952 | 84999.5336 | 77076.2802 | 69502.1429 | 62261.7391 | 55340.3636 | 48723.9593 | 42399.0886 | 36352.9058 | 105749.7679 | 96756.8568 | 88160.1935 | 79942.3183 | 72086.541 | 64576.9068 | 57398.1639 | 50535.7323 | 43975.6749 | 37704.6681 | 6.4616 | 1.9122 | 1.7496 | 1.5942 | 1.4456 | 1.3035 | 1.1677 | 1.0379 | 0.91382 | 0.79519 | 0.6818 | 902.5708 | 825.8166 | 752.4444 | 682.3051 | 615.2563 | 551.1618 | 489.8915 | 431.3208 | 375.331 | 321.8081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CV-G65 | Springfield | 202178 | 202178: CV-G65 L2P206 | 521921 | 654678 | 3PH | OH | Zone 1 | 173 | 413836.1 | 89.64% | 10.36% | 100% | 90% | 80.33% | 298.3489 | 276.1226 | 254.8756 | 234.5648 | 215.1489 | 196.5885 | 178.846 | 161.8852 | 145.6718 | 130.1727 | 34.4627 | 31.8953 | 29.4411 | 27.0949 | 24.8522 | 22.7082 | 20.6588 | 18.6996 | 16.8268 | 15.0365 | 6265.3275 | 5798.5743 | 5352.3873 | 4925.8603 | 4518.127 | 4128.3594 | 3755.7658 | 3399.5895 | 3059.1071 | 2733.6271 | 133887.7734 | 123913.4273 | 114378.5731 | 105263.8459 | 96550.7339 | 88221.541 | 80259.351 | 72647.9928 | 65372.008 | 58416.6194 | 140153.1009 | 129712.0016 | 119730.9604 | 110189.7061 | 101068.8609 | 92349.9004 | 84015.1167 | 76047.5822 | 68431.1151 | 61150.2465 | 3.2948 | 1.0492 | 0.97103 | 0.89631 | 0.82489 | 0.75661 | 0.69134 | 0.62894 | 0.5693 | 0.51228 | 0.45777 | 495.2204 | 458.3276 | 423.0603 | 389.347 | 357.1192 | 326.3114 | 296.8611 | 268.7084 | 241.7962 | 216.0698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BV-G43 | Springfield | 203031 | 203031: L43 P57 BV-G43 Mainline | Sub | 0 | 3PH | OH | Zone 1 | 716 | 275405.9 | 87.31% | 12.69% | 100% | 90% | 80.33% | 1838.9424 | 1701.9452 | 1570.9845 | 1445.7941 | 1326.1199 | 1211.7188 | 1102.3585 | 997.8169 | 897.8815 | 802.3496 | 267.3223 | 247.4074 | 228.3699 | 210.1713 | 192.7746 | 176.1444 | 160.247 | 145.0501 | 130.5227 | 116.6355 | 38617.7911 | 35740.8502 | 32990.6737 | 30361.6761 | 27848.518 | 25446.0953 | 23149.5287 | 20954.1539 | 18855.5122 | 16849.3414 | 1038547.146 | 961177.6563 | 887217.239 | 816515.6826 | 748929.3946 | 684321.1093 | 622559.6091 | 563519.4584 | 507080.7485 | 453128.8541 | 1077164.9371 | 996918.5065 | 920207.9127 | 846877.3588 | 776777.9127 | 709767.2046 | 645709.1378 | 584473.6123 | 525936.2608 | 469978.1955 | 20.9958 | 19.4779 | 18.0268 | 16.6397 | 15.3137 | 14.0461 | 12.8344 | 11.6761 | 10.5688 | 9.5103 | 8.4984 | 9193.5677 | 8508.667 | 7853.9446 | 7228.0707 | 6629.7742 | 6057.84 | 5511.1065 | 4988.4633 | 4488.8489 | 4011.2486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CS-G34 | Royalton | 203325 | 203325: Chelsea L6 Zone 2 L6 P327 | 0 | 0 | 3PH | OH | Zone 1 | 569 | 200972.7 | 83.09% | 16.91% | 100% | 90% | 80.33% | 769.47 | 712.1461 | 657.3481 | 604.9646 | 554.8893 | 507.0203 | 461.2606 | 417.5172 | 375.7012 | 335.7277 | 156.6271 | 144.9587 | 133.8045 | 123.1417 | 112.9488 | 103.205 | 93.8905 | 84.9864 | 76.4747 | 68.338 | 16158.869 | 14955.0686 | 13804.3103 | 12704.2571 | 11652.6746 | 10647.4272 | 9686.4733 | 8767.8611 | 7889.725 | 7050.2815 | 608496.2064 | 563164.5707 | 519830.3479 | 478405.5277 | 438805.9775 | 400951.2718 | 364764.5289 | 330172.2546 | 297104.1931 | 265493.1842 | 624655.0754 | 578119.6393 | 533634.6583 | 491109.7848 | 450458.6521 | 411598.699 | 374451.0021 | 338940.1157 | 304993.9181 | 272543.4658 | 1.3614 | 0.42675 | 0.39496 | 0.36457 | 0.33552 | 0.30774 | 0.2812 | 0.25582 | 0.23156 | 0.20837 | 0.1862 | 201.4265 | 186.4207 | 172.076 | 158.3635 | 145.2551 | 132.7243 | 120.7456 | 109.2948 | 98.3485 | 87.8845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TH-G16 | White River Jct | 203716 | 203716: RTE 5 L1 P.137 (tag: 4902 | Sub Breaker | 0 | 3PH | OH | Zone 1 | 123 | 111063.8 | 85.56% | 14.44% | 100% | 90% | 80.33% | 288.3764 | 266.893 | 246.3562 | 226.7243 | 207.9574 | 190.0174 | 172.8679 | 156.4741 | 140.8026 | 125.8216 | 48.6635 | 45.0382 | 41.5726 | 38.2597 | 35.0928 | 32.0654 | 29.1715 | 26.405 | 23.7604 | 21.2324 | 6055.9041 | 5604.7525 | 5173.4797 | 4761.2096 | 4367.1052 | 3990.3658 | 3630.2264 | 3285.9556 | 2956.8541 | 2642.2536 | 189057.7565 | 174973.3674 | 161509.5678 | 148639.0134 | 136335.5642 | 124574.2325 | 113331.1313 | 102583.4262 | 92309.289 | 82487.8532 | 195113.6606 | 180578.1199 | 166683.0475 | 153400.223 | 140702.6694 | 128564.5983 | 116961.3578 | 105869.3818 | 95266.1431 | 85130.1068 | 22.6996 | 2.9807 | 2.7586 | 2.5463 | 2.3434 | 2.1494 | 1.964 | 1.7868 | 1.6173 | 1.4553 | 1.3005 | 1406.87 | 1302.0613 | 1201.8706 | 1106.0946 | 1014.5387 | 927.017 | 843.3516 | 763.3728 | 686.918 | 613.8319 | 3924.2452 | 7675.5794 | 11261.6215 | 14689.6546 | 17966.6408 | 21099.2358 | 24093.8016 | 26956.4201 | 29692.9053 | 32308.8149 | 122510.0304 | 239621.9956 | 351573.7463 | 458592.6531 | 560896.068 | 658691.7663 | 752178.3679 | 841545.7412 | 926975.3887 | 1008640.8153
TH-G16 | White River Jct | 203723 | 203723: RTE 113 L1 Start at P.156 | 618564 | 619011 | 3PH | OH | Zone 2 | 830 | 58765.1 | 85.56% | 14.44% | 100% | 90% | 80.33% | 643.1594 | 595.2454 | 549.4427 | 505.6581 | 463.8027 | 423.7916 | 385.5435 | 348.9806 | 314.0288 | 280.6171 | 108.5332 | 100.4477 | 92.7185 | 85.3298 | 78.2667 | 71.5148 | 65.0605 | 58.8905 | 52.9924 | 47.3541 | 13506.3477 | 12500.1543 | 11538.2961 | 10618.8195 | 9739.8571 | 8899.6237 | 8096.4129 | 7328.5934 | 6594.6057 | 5892.9591 | 421651.2913 | 390239.1928 | 360211.1815 | 331506.2713 | 304066.1636 | 277835.1282 | 252759.8907 | 228789.5242 | 205875.3454 | 183970.8165 | 435157.639 | 402739.3472 | 371749.4776 | 342125.0908 | 313806.0207 | 286734.7519 | 260856.3036 | 236118.1175 | 212469.9511 | 189863.7756 | 7.1658 | 6.6477 | 6.1525 | 5.679 | 5.2265 | 4.7939 | 4.3803 | 3.985 | 3.6071 | 3.2458 | 2.9005 | 3137.7107 | 2903.9581 | 2680.5052 | 2466.8981 | 2262.7031 | 2067.5053 | 1880.9083 | 1702.5333 | 1532.0178 | 1369.0156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TH-G16 | White River Jct | 203724 | 203724: RTE 113 L1 P.217 | 653643 | 619011 | 3PH | OH | Zone 1 | 746 | 159190.9 | 85.56% | 14.44% | 100% | 90% | 80.33% | 1749.0145 | 1618.7168 | 1494.1602 | 1375.0919 | 1261.27 | 1152.4634 | 1048.451 | 949.0216 | 853.9733 | 763.1131 | 295.1462 | 273.1585 | 252.1395 | 232.0468 | 212.8393 | 194.4782 | 176.9261 | 160.1474 | 144.108 | 128.7753 | 36729.3046 | 33993.0518 | 31377.3644 | 28876.93 | 26486.6703 | 24201.7308 | 22017.4709 | 19929.4543 | 17933.4403 | 16025.3752 | 1146642.9784 | 1061220.5858 | 979562.0944 | 901501.6583 | 826880.7392 | 755547.7842 | 687357.9184 | 622172.6503 | 559859.5904 | 500292.1831 | 1183372.283 | 1095213.6376 | 1010939.4588 | 930378.5883 | 853367.4095 | 779749.515 | 709375.3893 | 642102.1045 | 577793.0308 | 516317.5583 | 22.6996 | 18.0778 | 16.731 | 15.4436 | 14.2129 | 13.0365 | 11.9119 | 10.8368 | 9.8091 | 8.8267 | 7.8875 | 8532.7237 | 7897.0545 | 7289.3942 | 6708.5089 | 6153.2186 | 5622.3957 | 5114.962 | 4629.8869 | 4166.1854 | 3722.9156 | 2068.4652 | 4045.7892 | 5935.9879 | 7742.9003 | 9470.196 | 11121.3833 | 12699.8155 | 14208.6985 | 15651.0968 | 17029.9397 | 64574.8982 | 126304.4823 | 185314.1232 | 241723.6677 | 295647.6818 | 347195.6835 | 396472.3653 | 443577.8065 | 488607.6769 | 531653.4307
TH-G16 | White River Jct | 203725 | 203725: Tucker Hill L1 294–333 | 618564 | 0 | 1PH | UG | Zone 3 | 293 | 130473.5 | 85.56% | 14.44% | 50% | 98% | 83.36% | 659.9609 | 603.8381 | 550.1882 | 498.9023 | 449.8761 | 403.0102 | 358.2092 | 315.3823 | 274.4425 | 235.3065 | 111.3684 | 101.8977 | 92.8443 | 84.1898 | 75.9166 | 68.008 | 60.4478 | 53.2208 | 46.3122 | 39.708 | 13859.1786 | 12680.6005 | 11553.9532 | 10476.9485 | 9447.399 | 8463.2137 | 7522.3939 | 6623.0286 | 5763.2915 | 4941.4362 | 432666.2329 | 395872.4977 | 360699.9766 | 327077.2352 | 294935.9868 | 264210.9535 | 234839.7338 | 206762.6755 | 179922.755 | 154265.4613 | 446525.4116 | 408553.0983 | 372253.9298 | 337554.1837 | 304383.3858 | 272674.1672 | 242362.1276 | 213385.7041 | 185686.0465 | 159206.8975 | 14.8563 | 6.8214 | 6.2413 | 5.6867 | 5.1567 | 4.6499 | 4.1655 | 3.7024 | 3.2598 | 2.8366 | 2.4321 | 3219.6782 | 2945.8783 | 2684.1426 | 2433.9395 | 2194.761 | 1966.1212 | 1747.5558 | 1538.6208 | 1338.892 | 1147.9637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DM-G6 | Brattleboro | 203953 | 203953: L.9-P.61 Quarry Rd | 555745 | 555590 | 1PH | UG | Zone 3 | 84 | 115667.1 | 89.45% | 10.55% | 50% | 98% | 83.36% | 116.579 | 106.6652 | 97.1882 | 88.1287 | 79.4685 | 71.1898 | 63.276 | 55.7108 | 48.479 | 41.5658 | 13.7552 | 12.5855 | 11.4673 | 10.3984 | 9.3765 | 8.3997 | 7.466 | 6.5734 | 5.7201 | 4.9044 | 2448.1585 | 2239.9682 | 2040.9513 | 1850.7035 | 1668.8384 | 1494.9868 | 1328.7954 | 1169.9268 | 1018.0582 | 872.8814 | 53439.0671 | 48894.6337 | 44550.4382 | 40397.6576 | 36427.8578 | 32632.9762 | 29005.3056 | 25537.4782 | 22222.451 | 19053.4914 | 55887.2256 | 51134.6019 | 46591.3895 | 42248.3611 | 38096.6962 | 34127.9629 | 30334.1009 | 26707.4049 | 23240.5093 | 19926.3728 | 39.4003 | 1.2436 | 1.1378 | 1.0367 | 0.94008 | 0.8477 | 0.75939 | 0.67497 | 0.59427 | 0.51713 | 0.44339 | 586.9595 | 537.0448 | 489.3293 | 443.7164 | 400.1132 | 358.4313 | 318.586 | 280.4964 | 244.0851 | 209.2781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DM-G6 | Brattleboro | 203954 | 203954: L633-Timson Hl Rd/Baker B | 489476 | 0 | 1PH | UG | Zone 3 | 75 | 159042 | 89.45% | 10.55% | 50% | 98% | 83.36% | 104.0884 | 95.2367 | 86.7751 | 78.6864 | 70.954 | 63.5624 | 56.4964 | 49.7418 | 43.2848 | 37.1123 | 12.2815 | 11.237 | 10.2387 | 9.2843 | 8.3719 | 7.4998 | 6.666 | 5.8691 | 5.1072 | 4.3789 | 2185.8558 | 1999.9716 | 1822.2779 | 1652.4138 | 1490.0343 | 1334.8096 | 1186.4244 | 1044.5775 | 908.9806 | 779.3584 | 47713.4528 | 43655.9229 | 39777.1769 | 36069.3371 | 32524.873 | 29136.5859 | 25897.5942 | 22801.3198 | 19841.4741 | 17012.0459 | 49899.3086 | 45655.8946 | 41599.4549 | 37721.7509 | 34014.9073 | 30471.3955 | 27084.0187 | 23845.8973 | 20750.4547 | 17791.4043 | 39.4003 | 1.1103 | 1.0159 | 0.92564 | 0.83935 | 0.75687 | 0.67803 | 0.60265 | 0.5306 | 0.46172 | 0.39588 | 524.071 | 479.5042 | 436.9012 | 396.1753 | 357.244 | 320.028 | 284.4518 | 250.4432 | 217.9331 | 186.8555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EL-G40 | White River Jct | 204106 | 204106: RTE 113 L3 P.141 to P192 | 621447 | 618847 | 3PH | OH | Zone 2 | 415 | 125173.7 | 85.29% | 14.71% | 100% | 90% | 80.33% | 421.0556 | 389.6879 | 359.7023 | 331.0379 | 303.6366 | 277.4426 | 252.4028 | 228.4663 | 205.5845 | 183.7109 | 72.6126 | 67.2031 | 62.032 | 57.0887 | 52.3633 | 47.846 | 43.5278 | 39.3999 | 35.4538 | 31.6816 | 8842.168 | 8183.4458 | 7553.7484 | 6951.7969 | 6376.3687 | 5826.2951 | 5300.4591 | 4797.7925 | 4317.2745 | 3857.9293 | 282099.9534 | 261084.1242 | 240994.2993 | 221789.677 | 203431.2531 | 185881.7424 | 169105.5022 | 153068.4607 | 137738.0469 | 123083.1254 | 290942.1214 | 269267.57 | 248548.0477 | 228741.4739 | 209807.6218 | 191708.0375 | 174405.9613 | 157866.2532 | 142055.3215 | 126941.0547 | 11.0221 | 1.8694 | 1.7301 | 1.597 | 1.4697 | 1.3481 | 1.2318 | 1.1206 | 1.0143 | 0.91274 | 0.81563 | 882.3441 | 816.6114 | 753.775 | 693.7073 | 636.2864 | 581.3955 | 528.9233 | 478.7631 | 430.8131 | 384.9758 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EL-G40 | White River Jct | 204107 | 204107: Beanville Rd L37 P.X2 P21 | 467089 | 620483 | 3PH | OH | Zone 3 | 279 | 82250.2 | 85.29% | 14.71% | 50% | 90% | 80.33% | 302.6059 | 280.0624 | 258.5123 | 237.9116 | 218.2187 | 199.3935 | 181.3978 | 164.1951 | 147.7503 | 132.0301 | 52.1855 | 48.2978 | 44.5814 | 41.0287 | 37.6326 | 34.3862 | 31.2827 | 28.316 | 25.4801 | 22.7691 | 6354.7238 | 5881.3108 | 5428.7574 | 4996.1445 | 4582.5935 | 4187.2645 | 3809.3546 | 3448.0962 | 3102.7557 | 2772.6317 | 202740.6951 | 187636.957 | 173198.7233 | 159396.6703 | 146202.7667 | 133590.2158 | 121533.4021 | 110007.8385 | 98990.1169 | 88457.8608 | 209095.4189 | 193518.2677 | 178627.4806 | 164392.8148 | 150785.3602 | 137777.4803 | 125342.7567 | 113455.9347 | 102092.8727 | 91230.4924 | 13.0078 | 3.9609 | 3.6658 | 3.3838 | 3.1141 | 2.8563 | 2.6099 | 2.3744 | 2.1492 | 1.934 | 1.7282 | 1869.5572 | 1730.2793 | 1597.1382 | 1469.8637 | 1348.1972 | 1231.8915 | 1120.7106 | 1014.4285 | 912.8295 | 815.7071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EL-G40 | White River Jct | 204108 | 204108: S.Vershire Rd L37 21 - 53 | 620828 | 620116 | 1PH | UG | Zone 3 | 146 | 115976.6 | 85.29% | 14.71% | 50% | 98% | 83.36% | 156.7493 | 143.4194 | 130.6769 | 118.4958 | 106.8514 | 95.7202 | 85.0794 | 74.9074 | 65.1837 | 55.8884 | 27.032 | 24.7332 | 22.5357 | 20.435 | 18.4269 | 16.5073 | 14.6723 | 12.9181 | 11.2412 | 9.6382 | 3291.7354 | 3011.8077 | 2744.2143 | 2488.4117 | 2243.8803 | 2010.1235 | 1786.6665 | 1573.0555 | 1368.8568 | 1173.6554 | 105019.3121 | 96088.5186 | 87551.2359 | 79390.1248 | 71588.6105 | 64130.8484 | 57001.6919 | 50186.6619 | 43671.9173 | 37444.227 | 108311.0475 | 99100.3264 | 90295.4502 | 81878.5365 | 73832.4908 | 66140.9718 | 58788.3584 | 51759.7174 | 45040.7741 | 38617.8824 | 13.0078 | 2.0518 | 1.8773 | 1.7105 | 1.551 | 1.3986 | 1.2529 | 1.1136 | 0.98049 | 0.85321 | 0.73154 | 968.4272 | 886.0726 | 807.3468 | 732.0897 | 660.1487 | 591.3775 | 525.6366 | 462.7923 | 402.7171 | 345.289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DM-G6 | Brattleboro | 204888 | 204888: Rt 30-Main Line feeder | Sub | 0 | 3PH | OH | Zone 1 | 1511 | 376214.4 | 89.45% | 10.55% | 100% | 90% | 80.33% | 5560.7991 | 5146.5317 | 4750.5179 | 4371.9533 | 4010.0692 | 3664.1304 | 3333.4345 | 3017.3098 | 2715.1142 | 2426.2341 | 656.1223 | 607.2426 | 560.5167 | 515.8496 | 473.1507 | 432.3331 | 393.3141 | 356.0144 | 320.3581 | 286.2729 | 116776.7804 | 108077.1658 | 99760.8756 | 91811.0198 | 84211.4523 | 76946.7387 | 70002.1246 | 63363.5057 | 57017.3992 | 50950.9163 | 2549035.2117 | 2359137.6666 | 2177607.431 | 2004075.8227 | 1838190.4042 | 1679614.2673 | 1528025.3488 | 1383115.7763 | 1244591.2428 | 1112170.4094 | 2665811.992 | 2467214.8324 | 2277368.3067 | 2095886.8424 | 1922401.8564 | 1756561.006 | 1598027.4734 | 1446479.282 | 1301608.642 | 1163121.3257 | 25.5222 | 23.677 | 21.9132 | 20.227 | 18.6151 | 17.0743 | 15.6013 | 14.1933 | 12.8473 | 11.5605 | 10.3305 | 11175.5667 | 10343.0115 | 9547.1404 | 8786.3373 | 8059.0568 | 7363.8219 | 6699.2206 | 6063.9032 | 5456.5792 | 4876.0153 | 1563.6776 | 3058.4561 | 4487.3713 | 5853.3253 | 7159.0923 | 8407.3243 | 9600.5564 | 10741.2121 | 11831.6079 | 12873.9585 | 34132.3783 | 66760.8079 | 97951.5561 | 127767.9703 | 156270.6068 | 183517.3535 | 209563.5478 | 234462.0886 | 258263.5442 | 281016.2546
DM-G6 | Brattleboro | 204889 | 204889: L6-Dover Rd-L61 P1-P121 | 554415 | 0 | 3PH | OH | Zone 2 | 316 | 94053.2 | 89.45% | 10.55% | 100% | 90% | 80.33% | 880.2761 | 814.6975 | 752.0084 | 692.0815 | 634.7951 | 580.0329 | 527.6837 | 477.641 | 429.8034 | 384.0736 | 103.8644 | 96.1267 | 88.73 | 81.6591 | 74.8999 | 68.4385 | 62.2617 | 56.3572 | 50.7128 | 45.3171 | 18485.7987 | 17108.6471 | 15792.1759 | 14533.7114 | 13330.6977 | 12180.6914 | 11081.3569 | 10030.4616 | 9025.8711 | 8065.545 | 403513.0234 | 373452.1862 | 344715.8965 | 317245.7919 | 290986.0814 | 265883.4323 | 241886.8619 | 218947.634 | 197019.1596 | 176056.9028 | 421998.8221 | 390560.8333 | 360508.0725 | 331779.5033 | 304316.779 | 278064.1237 | 252968.2189 | 228978.0956 | 206045.0307 | 184122.4478 | 56.6756 | 29.1486 | 26.9771 | 24.9012 | 22.9169 | 21.02 | 19.2066 | 17.4732 | 15.8161 | 14.2321 | 12.7178 | 13758.1256 | 12733.1754 | 11753.3867 | 10816.7697 | 9921.4222 | 9065.5256 | 8247.3418 | 7465.209 | 6717.5387 | 6002.8124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SB-G91 | Rutland | 204891 | 204891: WO212564 - L8 P298 thru P215 | 531232 | 652334 | 3PH | OH | Zone 2 | 544 | 241866.6 | 79.88% | 20.12% | 100% | 90% | 80.33% | 1798.138 | 1664.1807 | 1536.1258 | 1413.7133 | 1296.6946 | 1184.8319 | 1077.8982 | 975.6762 | 877.9584 | 784.5462 | 452.8504 | 419.114 | 386.8641 | 356.0353 | 326.5648 | 298.3929 | 271.4622 | 245.7183 | 221.1086 | 197.5833 | 37760.8987 | 34947.7944 | 32258.6417 | 29687.9791 | 27230.5857 | 24881.4704 | 22635.8625 | 20489.201 | 18437.1262 | 16475.4704 | 1759323.6426 | 1628257.8812 | 1502967.1698 | 1383197.0466 | 1268704.2622 | 1159256.2854 | 1054630.8306 | 954615.4068 | 859006.8858 | 767611.0894 | 1797084.5413 | 1663205.6756 | 1535225.8115 | 1412885.0257 | 1295934.8479 | 1184137.7558 | 1077266.6931 | 975104.6078 | 877444.012 | 784086.5598 | 11.2996 | 10.4826 | 9.7017 | 8.9552 | 8.2415 | 7.5594 | 6.9072 | 6.2838 | 5.6879 | 5.1182 | 4.5737 | 4947.8045 | 4579.2039 | 4226.8447 | 3890.0112 | 3568.0193 | 3260.2151 | 2965.9734 | 2684.6967 | 2415.8137 | 2158.7783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BV-G44 | Springfield | 204892 | 204892: L4-L43 poles 1 through 36 | 526443 | 0 | 3PH | OH | Zone 1 | 246 | 121491.7 | 85.77% | 14.23% | 100% | 90% | 80.33% | 467.8869 | 433.0303 | 399.7096 | 367.8571 | 337.4081 | 308.3007 | 280.4759 | 253.8771 | 228.4503 | 204.1439 | 77.6376 | 71.8538 | 66.3248 | 61.0394 | 55.987 | 51.1571 | 46.5401 | 42.1265 | 37.9073 | 33.8741 | 9825.6241 | 9093.6366 | 8393.9021 | 7724.9995 | 7085.5702 | 6474.3156 | 5889.9942 | 5331.4193 | 4797.4565 | 4287.0213 | 301622.1305 | 279151.9419 | 257671.8398 | 237138.199 | 217509.3163 | 198745.3259 | 180808.1187 | 163661.265 | 147269.9399 | 131600.8531 | 311447.7546 | 288245.5784 | 266065.7419 | 244863.1985 | 224594.8864 | 205219.6414 | 186698.1129 | 168992.6843 | 152067.3964 | 135887.8744 | 24.3714 | 4.4854 | 4.1513 | 3.8318 | 3.5265 | 3.2346 | 2.9555 | 2.6888 | 2.4338 | 2.19 | 1.957 | 2117.1171 | 1959.3965 | 1808.6255 | 1664.4977 | 1526.7205 | 1395.0141 | 1269.111 | 1148.7555 | 1033.703 | 923.7201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BV-G44 | Springfield | 204893 | 204893: L44 P65 thru P93 | 469709 | 0 | 1PH | UG | Zone 3 | 89 | 101209.5 | 85.77% | 14.23% | 50% | 98% | 83.36% | 246.2826 | 225.3389 | 205.3179 | 186.1792 | 167.8837 | 150.3944 | 133.6757 | 117.6936 | 102.4158 | 87.8111 | 40.8663 | 37.391 | 34.0689 | 30.8932 | 27.8574 | 24.9553 | 22.1811 | 19.5292 | 16.9941 | 14.5707 | 5171.9351 | 4732.1161 | 4311.6766 | 3909.7625 | 3525.5577 | 3158.2818 | 2807.1889 | 2471.566 | 2150.7313 | 1844.0333 | 158765.4955 | 145264.1516 | 132357.707 | 120019.9492 | 108225.8205 | 96951.3675 | 86173.692 | 75870.9049 | 66022.0816 | 56607.2195 | 163937.4306 | 149996.2677 | 136669.3836 | 123929.7117 | 111751.3783 | 100109.6493 | 88980.8809 | 78342.4709 | 68172.8129 | 58451.2528 | 11.6708 | 2.361 | 2.1602 | 1.9683 | 1.7848 | 1.6094 | 1.4418 | 1.2815 | 1.1283 | 0.98181 | 0.84181 | 1114.3915 | 1019.6242 | 929.0325 | 842.4325 | 759.6483 | 680.5117 | 604.8621 | 532.5458 | 463.4159 | 397.332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CV-G65 | Springfield | 204894 | 204894: L209 P1-P53 Tarbel Rd-Kna | 528262 | 0 | 1PH | UG | Zone 3 | 58 | 144583.9 | 89.64% | 10.36% | 50% | 98% | 83.36% | 64.4815 | 58.998 | 53.7561 | 48.7452 | 43.9551 | 39.3761 | 34.9988 | 30.8144 | 26.8144 | 22.9906 | 7.4484 | 6.8149 | 6.2095 | 5.6306 | 5.0773 | 4.5484 | 4.0428 | 3.5594 | 3.0974 | 2.6557 | 1354.1108 | 1238.9579 | 1128.8788 | 1023.6501 | 923.058 | 826.8982 | 734.9754 | 647.1029 | 563.1023 | 482.8029 | 28936.8571 | 26476.0802 | 24123.7307 | 21875.0309 | 19725.4138 | 17670.5137 | 15706.1571 | 13828.3544 | 12033.2918 | 10317.3238 | 30290.9679 | 27715.0381 | 25252.6095 | 22898.681 | 20648.4718 | 18497.4119 | 16441.1324 | 14475.4573 | 12596.3941 | 10800.1267 | 7.0795 | 1.0474 | 0.95834 | 0.8732 | 0.7918 | 0.71399 | 0.63961 | 0.56851 | 0.50054 | 0.43556 | 0.37345 | 494.3806 | 452.3387 | 412.1493 | 373.7307 | 337.0049 | 301.8973 | 268.3367 | 236.2548 | 205.5865 | 176.2695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DM-G6 | Brattleboro | 204895 | 204895: L65-South Wardsboro Rd | 554546 | 0 | 1PH | UG | Zone 3 | 137 | 195829.1 | 89.45% | 10.55% | 50% | 98% | 83.36% | 190.1348 | 173.9658 | 158.5093 | 143.7338 | 129.6093 | 116.1072 | 103.2001 | 90.8617 | 79.0669 | 67.7918 | 22.4341 | 20.5263 | 18.7026 | 16.9592 | 15.2927 | 13.6996 | 12.1766 | 10.7208 | 9.3292 | 7.9988 | 3992.8299 | 3653.2815 | 3328.6944 | 3018.4093 | 2721.796 | 2438.2522 | 2167.202 | 1908.0948 | 1660.4045 | 1423.628 | 87156.5737 | 79744.8192 | 72659.6432 | 65886.6558 | 59412.1013 | 53222.8302 | 47306.2722 | 41650.4109 | 36243.7594 | 31075.3371 | 91149.4036 | 83398.1008 | 75988.3376 | 68905.0651 | 62133.8974 | 55661.0824 | 49473.4741 | 43558.5057 | 37904.1639 | 32498.9651 | 39.4003 | 2.0282 | 1.8557 | 1.6908 | 1.5332 | 1.3826 | 1.2385 | 1.1008 | 0.96923 | 0.84341 | 0.72314 | 957.303 | 875.8944 | 798.0729 | 723.6803 | 652.5656 | 584.5844 | 519.5986 | 457.4763 | 398.0911 | 341.3227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DM-G6 | Brattleboro | 204896 | 204896: L94-Leonard Rd-Stickney B | 555912 | 0 | 1PH | UG | Zone 3 | 93 | 173964.9 | 89.45% | 10.55% | 50% | 98% | 83.36% | 129.0696 | 118.0936 | 107.6012 | 97.5711 | 87.983 | 78.8173 | 70.0555 | 61.6798 | 53.6731 | 46.0193 | 15.229 | 13.9339 | 12.6959 | 11.5125 | 10.3812 | 9.2997 | 8.2659 | 7.2776 | 6.3329 | 5.4298 | 2710.4612 | 2479.9648 | 2259.6247 | 2048.9932 | 1847.6426 | 1655.1639 | 1471.1663 | 1295.276 | 1127.1359 | 966.4044 | 59164.6814 | 54133.3444 | 49323.6994 | 44725.978 | 40330.8425 | 36129.3665 | 32113.0169 | 28273.6366 | 24603.4279 | 21094.9369 | 61875.1426 | 56613.3093 | 51583.324 | 46774.9712 | 42178.4851 | 37784.5304 | 33584.1832 | 29568.9126 | 25730.5638 | 22061.3413 | 39.4003 | 1.3768 | 1.2597 | 1.1478 | 1.0408 | 0.93852 | 0.84075 | 0.74729 | 0.65794 | 0.57254 | 0.49089 | 649.848 | 594.5853 | 541.7575 | 491.2574 | 442.9825 | 396.8347 | 352.7202 | 310.5496 | 270.2371 | 231.7008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DM-G6 | Brattleboro | 204897 | 204897: L911-P16 to End Hague Rd | 555716 | 556008 | 1PH | UG | Zone 3 | 63 | 57525.8 | 89.45% | 10.55% | 50% | 98% | 83.36% | 87.4342 | 79.9989 | 72.8911 | 66.0966 | 59.6014 | 53.3924 | 47.457 | 41.7831 | 36.3592 | 31.1743 | 10.3164 | 9.4391 | 8.6005 | 7.7988 | 7.0324 | 6.2998 | 5.5995 | 4.93 | 4.29 | 3.6783 | 1836.1189 | 1679.9762 | 1530.7135 | 1388.0276 | 1251.6288 | 1121.2401 | 996.5965 | 877.4451 | 763.5437 | 654.661 | 40079.3003 | 36670.9753 | 33412.8286 | 30298.2432 | 27320.8933 | 24474.7321 | 21753.9792 | 19153.1086 | 16666.8383 | 14290.1185 | 41915.4192 | 38350.9514 | 34943.5421 | 31686.2708 | 28572.5221 | 25595.9722 | 22750.5757 | 20030.5537 | 17430.382 | 14944.7796 | 39.4003 | 0.93267 | 0.85336 | 0.77754 | 0.70506 | 0.63577 | 0.56954 | 0.50623 | 0.4457 | 0.38785 | 0.33254 | 440.2196 | 402.7836 | 366.997 | 332.7873 | 300.0849 | 268.8235 | 238.9395 | 210.3723 | 183.0638 | 156.9586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CS-G34 | Royalton | 204898 | 204898: L61 P1 - P47 Russell Rd W | 616282 | 0 | 1PH | UG | Zone 3 | 106 | 179764 | 83.09% | 16.91% | 50% | 98% | 83.36% | 118.0067 | 107.9715 | 98.3784 | 89.2081 | 80.4417 | 72.0617 | 64.0509 | 56.3931 | 49.0727 | 42.0748 | 24.0205 | 21.9778 | 20.0251 | 18.1585 | 16.3741 | 14.6683 | 13.0377 | 11.4789 | 9.9888 | 8.5644 | 2478.1411 | 2267.4011 | 2065.9468 | 1873.3691 | 1689.2767 | 1513.2959 | 1345.0691 | 1184.2548 | 1030.5264 | 883.5716 | 93319.6168 | 85383.76 | 77797.5747 | 70545.6537 | 63613.2686 | 56986.3397 | 50651.4082 | 44595.6078 | 38806.6396 | 33272.7462 | 95797.7579 | 87651.1611 | 79863.5216 | 72419.0228 | 65302.5453 | 58499.6356 | 51996.4773 | 45779.8627 | 39837.166 | 34156.3177 | 2.3548 | 1.0812 | 0.98926 | 0.90137 | 0.81735 | 0.73703 | 0.66025 | 0.58685 | 0.51669 | 0.44962 | 0.3855 | 510.3302 | 466.932 | 425.446 | 385.7879 | 347.8773 | 311.6371 | 276.9937 | 243.8768 | 212.2191 | 181.9563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BV-G43 | Springfield | 204899 | 204899: L43 Brook Rd | 650740 | 0 | 1PH | UG | Zone 3 | 91 | 144198.3 | 87.31% | 12.69% | 50% | 98% | 83.36% | 99.5687 | 91.1014 | 83.0072 | 75.2697 | 67.8731 | 60.8024 | 54.0432 | 47.5819 | 41.4053 | 35.5008 | 14.474 | 13.2432 | 12.0665 | 10.9418 | 9.8665 | 8.8387 | 7.8561 | 6.9169 | 6.019 | 5.1607 | 2090.9425 | 1913.1297 | 1743.1518 | 1580.6634 | 1425.3347 | 1276.8501 | 1134.908 | 999.2203 | 869.5112 | 745.5174 | 56231.6567 | 51449.7428 | 46878.5307 | 42508.7363 | 38331.4849 | 34338.2925 | 30521.049 | 26872.0018 | 23383.7398 | 20049.1783 | 58322.5993 | 53362.8725 | 48621.6825 | 44089.3998 | 39756.8196 | 35615.1425 | 31655.957 | 27871.2221 | 24253.251 | 20794.6958 | 6.4616 | 1.0546 | 0.96494 | 0.8792 | 0.79725 | 0.71891 | 0.64401 | 0.57242 | 0.50398 | 0.43856 | 0.37602 | 497.7815 | 455.4504 | 414.9845 | 376.3016 | 339.3232 | 303.9741 | 270.1826 | 237.88 | 207.0007 | 177.4821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CH-G11 | Springfield | 204900 | 204900: L3135 Stage Rd | 513356 | 0 | 1PH | UG | Zone 3 | 76 | 289167.5 | 85.9% | 14.1% | 50% | 98% | 83.36% | 312.4006 | 285.8342 | 260.4384 | 236.1616 | 212.9544 | 190.7698 | 169.5628 | 149.2901 | 129.9107 | 111.3852 | 51.2843 | 46.9231 | 42.754 | 38.7687 | 34.959 | 31.3171 | 27.8357 | 24.5077 | 21.3264 | 18.2852 | 6560.4132 | 6002.5188 | 5469.2063 | 4959.3929 | 4472.0429 | 4006.1667 | 3560.818 | 3135.0923 | 2728.1251 | 2339.0898 | 199239.371 | 182296.1475 | 166099.4803 | 150616.4744 | 135815.6843 | 121667.05 | 108141.8361 | 95212.5733 | 82853.0026 | 71038.0222 | 205799.7842 | 188298.6663 | 171568.6867 | 155575.8673 | 140287.7272 | 125673.2166 | 111702.654 | 98347.6656 | 85581.1278 | 73377.112 | 20.331 | 4.7615 | 4.3566 | 3.9695 | 3.5995 | 3.2458 | 2.9076 | 2.5844 | 2.2754 | 1.9801 | 1.6977 | 2247.4281 | 2056.3079 | 1873.6088 | 1698.9599 | 1532.0064 | 1372.4092 | 1219.8443 | 1074.0017 | 934.5852 | 801.3118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BV-G44 | Springfield | 204901 | 204901: L434 P3 | 776981 | 489712 | 1PH | OH | Zone 3 | 113 | 225949.2 | 85.77% | 14.23% | 50% | 90% | 80.33% | 315.8949 | 292.3614 | 269.8649 | 248.3596 | 227.8019 | 208.15 | 189.364 | 171.4057 | 154.2388 | 137.8282 | 52.4172 | 48.5122 | 44.7793 | 41.2109 | 37.7997 | 34.5388 | 31.4216 | 28.4418 | 25.5932 | 22.8702 | 6633.793 | 6139.5899 | 5667.1626 | 5215.5514 | 4783.8392 | 4371.1492 | 3976.6433 | 3599.5202 | 3239.014 | 2894.3924 | 203640.8844 | 188470.0841 | 173967.7432 | 160104.4078 | 146851.9218 | 134183.37 | 122073.0228 | 110496.2845 | 99429.6431 | 88850.6227 | 210274.6774 | 194609.6741 | 179634.9058 | 165319.9591 | 151635.761 | 138554.5192 | 126049.6661 | 114095.8047 | 102668.6571 | 91745.0151 | 11.6708 | 3.0283 | 2.8027 | 2.5871 | 2.3809 | 2.1838 | 1.9954 | 1.8153 | 1.6432 | 1.4786 | 1.3213 | 1429.3766 | 1322.8911 | 1221.0977 | 1123.7895 | 1030.7689 | 941.847 | 856.8433 | 775.5849 | 697.907 | 623.6518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SB-G91 | Rutland | 204902 | 204902: L88 Rt100A, Spacer and CI | 532550 | 0 | 1PH | OH | Zone 3 | 135 | 151021.8 | 79.88% | 20.12% | 50% | 90% | 80.33% | 310.2657 | 287.1516 | 265.0559 | 243.9339 | 223.7425 | 204.4408 | 185.9895 | 168.3513 | 151.4903 | 135.3721 | 78.1386 | 72.3174 | 66.7528 | 61.4333 | 56.3482 | 51.4872 | 46.8404 | 42.3983 | 38.1519 | 34.0927 | 6515.5802 | 6030.1837 | 5566.1749 | 5122.6114 | 4698.5922 | 4293.2563 | 3905.7804 | 3535.3775 | 3181.2954 | 2842.815 | 303568.3644 | 280953.1855 | 259334.4819 | 238668.3467 | 218912.8074 | 200027.7413 | 181974.7933 | 164717.2985 | 148220.2075 | 132450.015 | 310083.9446 | 286983.3693 | 264900.6569 | 243790.958 | 223611.3996 | 204320.9976 | 185880.5737 | 168252.676 | 151401.5029 | 135292.83 | 3.8994 | 1.8088 | 1.674 | 1.5452 | 1.4221 | 1.3044 | 1.1918 | 1.0843 | 0.98144 | 0.88315 | 0.78918 | 853.7354 | 790.134 | 729.335 | 671.2149 | 615.6558 | 562.5447 | 511.7738 | 463.24 | 416.8446 | 372.4936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CS-G34 | Royalton | 205188 | 205188: L.6 P .251X - P166 | 616175 | 0 | 3PH | OH | Zone 1 | 871 | 207331.4 | 83.09% | 16.91% | 100% | 90% | 80.33% | 1177.8705 | 1090.1217 | 1006.2394 | 926.0531 | 849.3999 | 776.1243 | 706.0773 | 639.1168 | 575.1067 | 513.9171 | 239.7578 | 221.8964 | 204.8219 | 188.4999 | 172.897 | 157.9816 | 143.7234 | 130.0935 | 117.0641 | 104.6088 | 24735.281 | 22892.5567 | 21131.0269 | 19447.1141 | 17837.3982 | 16298.61 | 14827.6243 | 13421.4534 | 12077.2416 | 10792.2587 | 931459.0436 | 862067.3832 | 795733.2742 | 732321.994 | 671704.7564 | 613758.4494 | 558365.386 | 505413.0646 | 454793.9406 | 406405.2082 | 956194.3246 | 884959.9399 | 816864.3011 | 751769.1081 | 689542.1546 | 630057.0594 | 573193.0103 | 518834.518 | 466871.1822 | 417197.4669 | 1.3614 | 0.65325 | 0.60459 | 0.55806 | 0.51359 | 0.47108 | 0.43044 | 0.39159 | 0.35446 | 0.31896 | 0.28502 | 308.3348 | 285.3645 | 263.4064 | 242.4158 | 222.35 | 203.1684 | 184.832 | 167.3036 | 150.5475 | 134.5297 | 483.8364 | 946.3539 | 1388.4918 | 1811.1482 | 2215.1814 | 2601.4119 | 2970.6243 | 3323.5684 | 3660.9609 | 3983.4872 | 18219.8776 | 35636.9468 | 52286.581 | 68202.5952 | 83417.3143 | 97961.6389 | 111865.1082 | 125155.9595 | 137861.1863 | 150006.5925
CS-G34 | Royalton | 205534 | 205534: L6 P126 to P66 | 615615 | 617660 | 3PH | OH | Zone 1 | 244 | 140039.5 | 83.09% | 16.91% | 100% | 90% | 80.33% | 329.966 | 305.3843 | 281.8857 | 259.4224 | 237.949 | 217.4217 | 197.7989 | 179.0408 | 161.1091 | 143.9676 | 67.1652 | 62.1616 | 57.3784 | 52.8059 | 48.435 | 44.2566 | 40.2624 | 36.4441 | 32.7941 | 29.3049 | 6929.2865 | 6413.0698 | 5919.5988 | 5447.8712 | 4996.929 | 4565.8563 | 4153.7776 | 3759.8561 | 3383.2916 | 3023.3193 | 260936.8618 | 241497.6366 | 222914.9471 | 205151.0523 | 188169.8743 | 171936.925 | 156419.2356 | 141585.2902 | 127404.9616 | 113849.4498 | 267866.1483 | 247910.7065 | 228834.5459 | 210598.9235 | 193166.8033 | 176502.7813 | 160573.0132 | 145345.1463 | 130788.2531 | 116872.7692 | 1.3614 | 0.183 | 0.16937 | 0.15633 | 0.14388 | 0.13197 | 0.12058 | 0.1097 | 0.099297 | 0.089352 | 0.079845 | 86.3762 | 79.9414 | 73.7901 | 67.9098 | 62.2886 | 56.9152 | 51.7784 | 46.8681 | 42.174 | 37.6868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on CJ1: Andy Eiden: Taking Mitigation Scenario and scaling benefit by the % mitigated
Note on CT1: Andy Eiden: Taking Mitigation Scenario and scaling benefit by the % mitigated

## Mitigation Projects
FY2027 Projects - Cost Estimate Worksheet (Source: Provided by GMP) | [15 empty] | Percent of customers by class |  |  |  |  | Outages PRE mitigation |  | Outages Post Mitigation |  | Post Mitigation Consequences |  |  | Non-storm restoration costs |  |  |  | Feeder Backup Value
Circuit | District | Project | Name | Start Tag | Protective device | Phase | OH/UG | Distance | Zone | Customers on project | Construction Cost Estimate (fully loaded) | Feeder Backup? | Customers on feeder backup | Feeder Backed Up | Customers Backed Up on Other Feeder | RES % | NONRES % | Percent of Customers Impacted by Mitigation | Effectiveness Score | Applicability Score | RES | NONRES | RES | NONRES | RES | NONRES | Total | Number of non-storm Incidents (pre-mitigation) (per Zone) | Times the Downstream applicability factor and multi-project weighting | Restoration Cost - Pre | Restoration Cost - Post Mitigation | RES | NONRES | Total
CV-G65 | Springfield | 175351 | 175351: Cavendish line 2 | 520170 | Sub Breaker | 3PH | OH | 1.2 | Zone 1 | 331 | 917484 | Main line feed backs up BV-G44 | 339 Customers on CV-G65 and 792 on BV-G44 | BV-G44 | 792 | 89.64% | 10.36% | 100% | 90% | 80.33% | 615.3151 | 71.076 | 170.4583 | 19.6899 | 3579.6243 | 55899.6337 | 59479.258 | 3.2948 | 2.1639 | 1021.3432 | 282.9386 | 26897.7697 | 574795.5742 | 601693.3439
EL-G40 | White River Jct | 197817 | 197817: ELY-129 G40 Zone 1 LC | 620436 | 0 | 3PH | OH | 2.4 | Zone 2 | 1015 | 1782012 |  |  |  |  | 85.29% | 14.71% | 100% | 90% | 80.33% | 1110.0656 | 191.4349 | 307.517 | 53.0325 | 6457.858 | 150559.1353 | 157016.9933 | 11.0221 | 4.9284 | 2326.2005 | 644.418
DM-G6 | Brattleboro | 199297 | 199297: L66 P15-1 to L62 P140 | 554333 | 554331 | 3PH | OH | 3.3 | Zone 2 | 254 | 2456234 |  |  |  |  | 89.45% | 10.55% | 100% | 90% | 80.33% | 762.7053 | 89.9921 | 211.2892 | 24.9302 | 4437.0736 | 70776.7053 | 75213.7789 | 56.6756 | 25.2555 | 11920.573 | 3302.3088
SH-G35 | Royalton | 199309 | 199309: Fay Brook Rd. | 599580 | 476994 | 1PH | UG | 1.2 | Zone 3 | 210 | 694311 |  |  |  |  | 86.72% | 13.28% | 50% | 98% | 83.36% | 422.0844 | 64.6436 | 77.2751 | 11.8349 | 1622.7781 | 33599.3739 | 35222.152 | 25.1076 | 5.3366 | 2518.8906 | 461.1581
SH-G35 | Royalton | 199373 | 199373: FAY BROOK RD P.44 -P.75 | 617377 | 476994 | 1PH | UG | 1.5 | Zone 3 | 135 | 867921 |  |  |  |  | 86.72% | 13.28% | 50% | 98% | 83.36% | 271.34 | 41.5566 | 49.6769 | 7.6082 | 1043.2145 | 21599.5975 | 22642.812 | 25.1076 | 3.4307 | 1619.2868 | 296.4588
EL-G40 | White River Jct | 199494 | 199494: L3P52 | 619216 | 620436 | 3PH | OH | 3 | Zone 2 | 840 | 2227005 |  |  |  |  | 85.29% | 14.71% | 100% | 90% | 80.33% | 918.675 | 158.4289 | 254.4969 | 43.8889 | 5344.4342 | 124600.6637 | 129945.0979 | 11.0221 | 4.0787 | 1925.1314 | 533.3115
SH-G35 | Royalton | 199498 | 199498: Brk Rd. P.75-L.81P.76 | 617059 | 476994, 618154 | 1PH | UG | 3 | Zone 3 | 107 | 1735452 |  |  |  |  | 86.72% | 13.28% | 50% | 98% | 83.36% | 215.0621 | 32.9374 | 39.3735 | 6.0302 | 826.8441 | 17119.681 | 17946.5251 | 25.1076 | 2.7191 | 1283.4347 | 234.971
SH-G35 | Royalton | 199569 | 199569: Brook Rd. P.76 to 50X | 618225 | 618154 | 1PH | UG | 1.7 | Zone 3 | 42 | 978528 |  |  |  |  | 86.72% | 13.28% | 50% | 98% | 83.36% | 84.4169 | 12.9287 | 15.455 | 2.367 | 324.5556 | 6719.8748 | 7044.4304 | 25.1076 | 1.0673 | 503.7781 | 92.2316
DM-G6 | Brattleboro | 199616 | 199616: Newfane L66 P1-105 | 556104 | 0 | 1PH | OH | 2.5 | Zone 3 | 363 | 1258653 |  |  |  |  | 89.45% | 10.55% | 50% | 90% | 80.33% | 548.6043 | 64.7302 | 151.9777 | 17.9319 | 3191.531 | 50908.7898 | 54100.3208 | 39.4003 | 5.852 | 2762.1492 | 765.1872
DM-G6 | Brattleboro | 199621 | 199621: Brookline L62 P140-195 | 472083 | 0 | 1PH | OH | 4.75 | Zone 3 | 43 | 2385224 |  |  |  |  | 89.45% | 10.55% | 50% | 90% | 80.33% | 64.9862 | 7.6678 | 18.0029 | 2.1242 | 378.0601 | 6030.5178 | 6408.5779 | 39.4003 | 0.69321 | 327.1967 | 90.642
BV-G44 | Springfield | 199623 | 199623: BV Sub to L4 P126 | Sub breaker | 0 | 3PH | OH | 1.5 | Zone 1 | 797 | 1109903 | Main line feed that backs up to CV-G65 | 339 Customers on CV-G65 and 792 on BV-G44 |  |  | 85.77% | 14.23% | 100% | 90% | 80.33% | 1634.0122 | 271.1356 | 452.6639 | 75.1116 | 9505.9416 | 213241.9128 | 222747.8544 | 24.3714 | 15.6645 | 7393.6574 | 2048.2355
BV-G44 | Springfield | 199973 | 199973: L41 VT Route 106 - Spacer | 526376 | 0 | 3PH | OH | 2.1 | Zone 1 | 197 | 1553533 | Main line feed that backs up to CV-G65 | 339 Customers on CV-G65 and 792 on BV-G44 | CV-G65 | 339 | 85.77% | 14.23% | 100% | 90% | 80.33% | 403.8901 | 67.0185 | 111.8881 | 18.5659 | 2349.6493 | 52708.4778 | 55058.1271 | 24.3714 | 3.8719 | 1827.5414 | 506.2765 | 1631.7268 | 50089.9396 | 51721.6664
CV-G65 | Springfield | 201142 | 201142: L208 HIGH ST. - CIC |  |  | 1PH | UG | 1.9 | Zone 3 | 122 | 1076503 |  |  |  |  | 89.64% | 10.36% | 50% | 98% | 83.36% | 147.6993 | 17.061 | 27.0408 | 3.1235 | 567.856 | 8867.6741 | 9435.53 | 7.0795 | 2.3992 | 1132.4132 | 207.322
DM-G6 | Brattleboro | 201143 | 201143: L61 DOVER RD. - CIC | 498311 | 0 | 1PH | UG | 4.25 | Zone 3 | 170 | 2458013 |  |  |  |  | 89.45% | 10.55% | 50% | 98% | 83.36% | 256.9221 | 30.3144 | 47.0373 | 5.55 | 987.7825 | 15756.3286 | 16744.1111 | 39.4003 | 2.7406 | 1293.5685 | 236.8263
DM-G6 | Brattleboro | 201149 | 201149: L6 VT RT 30 - CIC | 476653 | 0 | 1PH | UG | 4.35 | Zone 3 | 194 | 2515767 |  |  |  |  | 89.45% | 10.55% | 50% | 98% | 83.36% | 293.1935 | 34.5941 | 53.6778 | 6.3335 | 1127.2341 | 17980.7514 | 19107.9856 | 39.4003 | 3.1275 | 1476.1899 | 270.2606
CH-G11 | Springfield | 201152 | 201152: L342 TOWNSHEND RD | 488351 | 0 | 1PH | OH | 5.2 | Zone 3 | 73 | 2617704 |  |  |  |  | 85.9% | 14.1% | 50% | 90% | 80.33% | 326.763 | 53.642 | 90.5218 | 14.8602 | 1900.9586 | 42188.2 | 44089.1586 | 20.331 | 4.9804 | 2350.7515 | 651.2193
BV-G43 | Springfield | 201153 | 201153: L438 BROWNSVILLE - CIC | 0 | 0 | 1PH | UG | 1.5 | Zone 3 | 165 | 1442345 |  |  |  |  | 87.31% | 12.69% | 50% | 98% | 83.36% | 196.597 | 28.5788 | 35.993 | 5.2322 | 755.8521 | 14854.2236 | 15610.0757 | 6.4616 | 2.0823 | 982.8629 | 179.9424
CV-G65 | Springfield | 202178 | 202178: CV-G65 L2P206 | 521921 | 654678 | 3PH | OH | 5.5 | Zone 1 | 173 | 4138361 | Main line feed backs up BV-G44 | 339 Customers on CV-G65 and 792 on BV-G44 |  |  | 89.64% | 10.36% | 100% | 90% | 80.33% | 321.5998 | 37.1485 | 89.0915 | 10.2911 | 1870.9215 | 29216.4248 | 31087.3463 | 3.2948 | 1.131 | 533.8138 | 147.8803
BV-G43 | Springfield | 203031 | 203031: L43 P57 BV-G43 Mainline | Sub | 0 | 3PH | OH | 3.7 | Zone 1 | 716 | 2754059 |  |  |  |  | 87.31% | 12.69% | 100% | 90% | 80.33% | 1982.2543 | 288.1552 | 549.136 | 79.8265 | 11531.856 | 226627.375 | 238159.2311 | 20.9958 | 20.9958 | 9910.0376 | 2745.3382
CS-G34 | Royalton | 203325 | 203325: Chelsea L6 Zone 2 L6 P327 | 0 | 0 | 3PH | OH | 2.7 | Zone 1 | 569 | 2009727 | Maineline Feeder backup to BE-G29 | 1877 customers on the BE-G29 would be backed up and 871 on the CS-G34 |  |  | 83.09% | 16.91% | 100% | 90% | 80.33% | 829.436 | 168.8333 | 229.7754 | 46.7712 | 4825.2825 | 132783.474 | 137608.7565 | 1.3614 | 0.46001 | 217.124 | 60.149
TH-G16 | White River Jct | 203716 | 203716: RTE 5 L1 P.137 (tag: 4902 | Sub Breaker | 0 | 3PH | OH | 1.5 | Zone 1 | 123 | 1110638 | Main line backs up EL-G40 | 1005 Customers on the EL-G40 and 1010 on the TH-G16 | EL-G40 | 1005 | 85.56% | 14.44% | 100% | 90% | 80.33% | 310.85 | 52.4559 | 86.1135 | 14.5317 | 1808.3845 | 41255.3857 | 43063.7702 | 22.6996 | 3.2129 | 1516.5097 | 420.1126 | 39242.4522 | 1225100.3044 | 1264342.7566
TH-G16 | White River Jct | 203723 | 203723: RTE 113 L1 Start at P.156 | 618564 | 619011 | 3PH | OH | 0.8 | Zone 2 | 830 | 587651 |  |  |  |  | 85.56% | 14.44% | 100% | 90% | 80.33% | 693.2819 | 116.9913 | 192.0571 | 32.4096 | 4033.1995 | 92010.9652 | 96044.1648 | 7.1658 | 7.1658 | 3382.2377 | 936.9678
TH-G16 | White River Jct | 203724 | 203724: RTE 113 L1 P.217 | 653643 | 619011 | 3PH | OH | 2.15 | Zone 1 | 746 | 1591909 | Main line backs up EL-G40 | 1005 Customers on the EL-G40 and 1010 on the TH-G16 | EL-G41 | 722 | 85.56% | 14.44% | 100% | 90% | 80.33% | 1885.3181 | 318.1474 | 522.2822 | 88.1351 | 10967.9254 | 250215.5914 | 261183.5168 | 22.6996 | 19.4866 | 9197.693 | 2548.0003 | 20684.6521 | 645748.9821 | 666433.6341
TH-G16 | White River Jct | 203725 | 203725: Tucker Hill L1 294–333 | 618564 | 0 | 1PH | UG | 2.25 | Zone 3 | 293 | 1304735 |  |  |  |  | 85.56% | 14.44% | 50% | 98% | 83.36% | 718.6705 | 121.2757 | 131.5741 | 22.2031 | 2763.0558 | 63034.6765 | 65797.7322 | 14.8563 | 7.4282 | 3506.0985 | 641.8959
DM-G6 | Brattleboro | 203953 | 203953: L.9-P.61 Quarry Rd | 555745 | 555590 | 1PH | UG | 2 | Zone 3 | 84 | 1156671 |  |  |  |  | 89.45% | 10.55% | 50% | 98% | 83.36% | 126.9498 | 14.9789 | 23.2419 | 2.7423 | 488.0808 | 7785.48 | 8273.5608 | 39.4003 | 1.3542 | 639.175 | 117.0201
DM-G6 | Brattleboro | 203954 | 203954: L633-Timson Hl Rd/Baker B | 489476 | 0 | 1PH | UG | 2.75 | Zone 3 | 75 | 1590420 |  |  |  |  | 89.45% | 10.55% | 50% | 98% | 83.36% | 113.348 | 13.374 | 20.7517 | 2.4485 | 435.7864 | 6951.3214 | 7387.1078 | 39.4003 | 1.2091 | 570.692 | 104.4822
EL-G40 | White River Jct | 204106 | 204106: RTE 113 L3 P.141 to P192 | 621447 | 618847 | 3PH | OH | 1.7 | Zone 2 | 415 | 1251737 |  |  |  |  | 85.29% | 14.71% | 100% | 90% | 80.33% | 453.8692 | 78.2714 | 125.7336 | 21.6832 | 2640.405 | 61558.6612 | 64199.0662 | 11.0221 | 2.0151 | 951.1066 | 263.4813
EL-G40 | White River Jct | 204107 | 204107: Beanville Rd L37 P.X2 P21 | 467089 | 620483 | 3PH | OH | 1.12 | Zone 3 | 279 | 822502 |  |  |  |  | 85.29% | 14.71% | 50% | 90% | 80.33% | 326.1885 | 56.2524 | 90.3627 | 15.5834 | 1897.6165 | 44241.2188 | 46138.8354 | 13.0078 | 4.2696 | 2015.2549 | 558.278
EL-G40 | White River Jct | 204108 | 204108: S.Vershire Rd L37 21 - 53 | 620828 | 620116 | 1PH | UG | 2 | Zone 3 | 146 | 1159766 |  |  |  |  | 85.29% | 14.71% | 50% | 98% | 83.36% | 170.6936 | 29.4367 | 31.2506 | 5.3893 | 656.2617 | 15300.1502 | 15956.4119 | 13.0078 | 2.2343 | 1054.5778 | 193.0719
DM-G6 | Brattleboro | 204888 | 204888: Rt 30-Main Line feeder | Sub | 0 | 3PH | OH | 5 | Zone 1 | 1511 | 3762144 | Mainline feed that backs up to EJ-G7 | 2571 Customers on the EJ-G7 and 1907 on the DM-G6 | EJ-G7 | 2571 | 89.45% | 10.55% | 100% | 90% | 80.33% | 5994.1613 | 707.255 | 1660.5386 | 195.928 | 34871.3114 | 556239.7058 | 591111.0171 | 25.5222 | 25.5222 | 12046.4971 | 3337.1931 | 15636.7759 | 341323.7832 | 356960.5592
DM-G6 | Brattleboro | 204889 | 204889: L6-Dover Rd-L61 P1-P121 | 554415 | 0 | 3PH | OH | 4 | Zone 2 | 316 | 940532 |  |  |  |  | 89.45% | 10.55% | 100% | 90% | 80.33% | 948.8775 | 111.9587 | 262.8638 | 31.0155 | 5520.1388 | 88052.909 | 93573.0478 | 56.6756 | 31.4202 | 14830.3191 | 4108.3842
SB-G91 | Rutland | 204891 | 204891: WO212564 - L8 P298 thru P215 | 531232 | 652334 | 3PH | OH | 3.3 | Zone 2 | 544 | 2418666 |  |  |  |  | 79.88% | 20.12% | 100% | 90% | 80.33% | 1938.2699 | 488.1417 | 536.9512 | 135.228 | 11275.975 | 383912.1801 | 395188.1551 | 11.2996 | 11.2996 | 5333.3951 | 1477.4892
BV-G44 | Springfield | 204892 | 204892: L4-L43 poles 1 through 36 | 526443 | 0 | 3PH | OH | 1.65 | Zone 1 | 246 | 1214917 | Main line feed that backs up to CV-G65 | 339 Customers on CV-G65 and 792 on BV-G44 | CV-G65 | 339 | 85.77% | 14.23% | 100% | 90% | 80.33% | 504.3501 | 83.688 | 139.7181 | 23.1838 | 2934.0798 | 65818.7083 | 68752.7882 | 24.3714 | 4.835 | 2282.1076 | 632.2032
BV-G44 | Springfield | 204893 | 204893: L44 P65 thru P93 | 469709 | 0 | 1PH | UG | 1.75 | Zone 3 | 89 | 1012095 |  |  |  |  | 85.77% | 14.23% | 50% | 98% | 83.36% | 268.1917 | 44.5017 | 49.1005 | 8.1474 | 1031.1105 | 23130.3737 | 24161.4842 | 11.6708 | 2.571 | 1213.527 | 222.1723
CV-G65 | Springfield | 204894 | 204894: L209 P1-P53 Tarbel Rd-Kna | 528262 | 0 | 1PH | UG | 2.5 | Zone 3 | 58 | 1445839 |  |  |  |  | 89.64% | 10.36% | 50% | 98% | 83.36% | 70.2177 | 8.111 | 12.8554 | 1.485 | 269.9643 | 4215.7795 | 4485.7438 | 7.0795 | 1.1406 | 538.3604 | 98.5629
DM-G6 | Brattleboro | 204895 | 204895: L65-South Wardsboro Rd | 554546 | 0 | 1PH | UG | 3.35 | Zone 3 | 137 | 1958291 |  |  |  |  | 89.45% | 10.55% | 50% | 98% | 83.36% | 207.049 | 24.4298 | 37.9065 | 4.4726 | 796.0365 | 12697.7472 | 13493.7836 | 39.4003 | 2.2086 | 1042.464 | 190.8541
DM-G6 | Brattleboro | 204896 | 204896: L94-Leonard Rd-Stickney B | 555912 | 0 | 1PH | UG | 3 | Zone 3 | 93 | 1739649 |  |  |  |  | 89.45% | 10.55% | 50% | 98% | 83.36% | 140.5515 | 16.5838 | 25.7321 | 3.0362 | 540.3751 | 8619.6386 | 9160.0137 | 39.4003 | 1.4993 | 707.6581 | 129.5579
DM-G6 | Brattleboro | 204897 | 204897: L911-P16 to End Hague Rd | 555716 | 556008 | 1PH | UG | 1 | Zone 3 | 63 | 575258 |  |  |  |  | 89.45% | 10.55% | 50% | 98% | 83.36% | 95.2123 | 11.2342 | 17.4315 | 2.0567 | 366.0606 | 5839.11 | 6205.1706 | 39.4003 | 1.0156 | 479.3813 | 87.765
CS-G34 | Royalton | 204898 | 204898: L61 P1 - P47 Russell Rd W | 616282 | 0 | 1PH | UG | 3.1 | Zone 3 | 106 | 1797640 |  |  |  |  | 83.09% | 16.91% | 50% | 98% | 83.36% | 128.5045 | 26.1573 | 23.5266 | 4.7889 | 494.0583 | 13595.6342 | 14089.6925 | 2.3548 | 1.1774 | 555.7288 | 101.7427
BV-G43 | Springfield | 204899 | 204899: L43 Brook Rd | 650740 | 0 | 1PH | UG | 1.5 | Zone 3 | 91 | 1441983 |  |  |  |  | 87.31% | 12.69% | 50% | 98% | 83.36% | 108.4262 | 15.7616 | 19.8507 | 2.8856 | 416.8639 | 8192.3294 | 8609.1932 | 6.4616 | 1.1484 | 542.0638 | 99.2409
CH-G11 | Springfield | 204900 | 204900: L3135 Stage Rd | 513356 | 0 | 1PH | UG | 5 | Zone 3 | 76 | 2891675 |  |  |  |  | 85.9% | 14.1% | 50% | 98% | 83.36% | 340.1916 | 55.8465 | 62.2822 | 10.2244 | 1307.9265 | 29026.9689 | 30334.8954 | 20.331 | 5.1851 | 2447.3577 | 448.0619
BV-G44 | Springfield | 204901 | 204901: L434 P3 | 776981 | 489712 | 1PH | OH | 4.5 | Zone 3 | 113 | 2259492 |  |  |  |  | 85.77% | 14.23% | 50% | 90% | 80.33% | 340.5131 | 56.5022 | 94.331 | 15.6526 | 1980.9508 | 44437.6543 | 46418.6052 | 11.6708 | 3.2643 | 1540.7702 | 426.8334
SB-G91 | Rutland | 204902 | 204902: L88 Rt100A, Spacer and CI | 532550 | 0 | 1PH | OH | 3 | Zone 3 | 135 | 1510218 |  |  |  |  | 79.88% | 20.12% | 50% | 90% | 80.33% | 334.4452 | 84.228 | 92.65 | 23.3334 | 1945.6507 | 66243.4073 | 68189.058 | 3.8994 | 1.9497 | 920.2684 | 254.9383
CS-G34 | Royalton | 205188 | 205188: L.6 P .251X - P166 | 616175 | 0 | 3PH | OH | 2.8 | Zone 1 | 871 | 2073314 | Maineline Feeder backup to BE-G29 | 1877 customers on the BE-G29 would be backed up and 871 on the CS-G34 | BE-G29 | 1877 | 83.09% | 16.91% | 100% | 90% | 80.33% | 1269.6639 | 258.4425 | 351.7299 | 71.5953 | 7386.3287 | 203259.0613 | 210645.39 | 1.3614 | 0.70416 | 332.3638 | 92.0734 | 4838.364 | 182198.7761 | 187037.1401
CS-G34 | Royalton | 205534 | 205534: L6 P126 to P66 | 615615 | 617660 | 3PH | OH | 1.9 | Zone 1 | 244 | 1400395 |  |  | BE-G29 | 1877 | 83.09% | 16.91% | 100% | 90% | 80.33% | 355.6808 | 72.3995 | 98.5328 | 20.0565 | 2069.1897 | 56940.5407 | 59009.7304 | 1.3614 | 0.19726 | 93.1077 | 25.7932
Note on P3: Andy Eiden: Only count one feeder backup value per feeder
Note on AG47: Andy Eiden: De-rated by 50% because of substation size limitations.
Note on AH47: Andy Eiden: De-rated by 50% because of substation size limitations.

## Customer Count by class
Source: Data provided by GMP
|  | Single Phase Count |  |  | Multi Phase Count (2 & 3 Phase) |  |  | Total
| Feeder | C&I | Res | Total | C&I | Res | Total | C&I | Res | Total | % C&I | % Res
| BV-G43 | 57 | 483 | 540 | 34 | 143 | 177 | 91 | 626 | 717 | 12.69% | 87.31%
| BV-G44 | 88 | 585 | 673 | 25 | 96 | 121 | 113 | 681 | 794 | 14.23% | 85.77%
| CH-G11 | 81 | 711 | 792 | 61 | 154 | 215 | 142 | 865 | 1007 | 14.1% | 85.9%
| CS-G34 | 87 | 558 | 645 | 62 | 174 | 236 | 149 | 732 | 881 | 16.91% | 83.09%
| CV-G65 | 31 | 282 | 313 | 4 | 21 | 25 | 35 | 303 | 338 | 10.36% | 89.64%
| DM-G6 | 131 | 1471 | 1602 | 71 | 241 | 312 | 202 | 1712 | 1914 | 10.55% | 89.45%
| EL-G40 | 113 | 713 | 826 | 36 | 151 | 187 | 149 | 864 | 1013 | 14.71% | 85.29%
| SB-G91 | 133 | 591 | 724 | 106 | 358 | 464 | 239 | 949 | 1188 | 20.12% | 79.88%
| SH-G35 | 115 | 971 | 1086 | 55 | 139 | 194 | 170 | 1110 | 1280 | 13.28% | 86.72%
| TH-G16 | 102 | 842 | 944 | 60 | 118 | 178 | 162 | 960 | 1122 | 14.44% | 85.56%
|  | 938 | 7207 | 8145 | 514 | 1595 | 2109 | 1452 | 8802 | 10254

## Historical outage summary
Source: Data provided by GMP
Customers over time
| Feeder | 2020 | 2021 | 2022 | 2023 | 2024 | 5-yr average
| BV-G44 | 780 | 783 | 786 | 782 | 788 | 783.8
| CH-G11 | 1597 | 1597 | 1624 | 1633 | 1635 | 1617.2
| CV-G65 | 321 | 317 | 322 | 331 | 333 | 324.8
| EL-G40 | 996 | 1005 | 1009 | 1020 | 1017 | 1009.4
| TH-G16 | 1092 | 1114 | 1107 | 1121 | 1121 | 1111
| SH-G35 | 1336 | 1341 | 1358 | 1273 | 1269 | 1315.4
| DM-G6 | 1836 | 1851 | 1873 | 1880 | 1919 | 1871.8
| SB-G91 | 1178 | 1177 | 1178 | 1177 | 1175 | 1177
| BV-G43 | 647 | 668 | 670 | 708 | 711 | 680.8
| CS-G34 | 859 | 858 | 865 | 873 | 871 | 865.2
| EL-G41 | 704 | 707 | 708 | 715 | 731 | 713
| EJ-G7 | 2615 | 2634 | 2662 | 2743 | 2648 | 2660.4
| BE-G29 | 1718 | 1617 | 1755 | 1869 | 1860 | 1763.8
Total Customers Out
| Feeder | 2020 | 2021 | 2022 | 2023 | 2024 | 5-yr average
| BV-G44 | 4788 | 5482 | 3989 | 5788 | 5543 | 5118
| CH-G11 | 9039 | 7623 | 10581 | 18609 | 7913 | 10753
| CV-G65 | 1314 | 1199 | 1969 | 2082 | 1082 | 1529.2
| EL-G40 | 10915 | 3061 | 10712 | 6608 | 5837 | 7426.6
| TH-G16 | 6804 | 5046 | 7112 | 1891 | 4542 | 5079
| SH-G35 | 7262 | 12256 | 6043 | 4576 | 7308 | 7489
| DM-G6 | 13987 | 9921 | 11196 | 16260 | 11487 | 12570.2
| SB-G91 | 5818 | 4989 | 9348 | 4410 | 11014 | 7115.8
| BV-G43 | 1283 | 2244 | 4498 | 4126 | 2944 | 3019
| CS-G34 | 3242 | 1927 | 3779 | 4394 | 5271 | 3722.6
| EL-G41 | 2038 | 1053 | 4398 | 1336 | 1318 | 2028.6
| EJ-G7 | 14229 | 21778 | 25933 | 31550 | 22547 | 23207.4
| BE-G29 | 6845 | 6824 | 10358 | 4842 | 4925 | 6758.8

## Pre_Post mitigation outages
Mitigation ("Accelerated") Scenario
| As-is results based on historical 5-yr average (2020-2024) |  |  |  | Pre-Mitigation Applicable Outages |  |  | Post-Mitigation Applicable Outages
Customer adjustment factor (2025 / Avg baseline) | FEEDER_ID | Customers | Outages | Current Customers (2025) | Res | Nonres | Total | Res | Nonres | Total | Feeder back-up outages reduced
1.0532 | BV-G43 | 680.8 | 3179.5285 | 717 | 2287.2776 | 332.4956 | 2619.7732 | 604.9796 | 87.9443 | 692.9239
1.013 | BV-G44 | 783.8 | 5184.6032 | 794 | 3150.9572 | 522.8461 | 3673.8032 | 847.7015 | 140.6612 | 988.3627 | 1428.7987
0.62268 | CH-G11 | 1617.2 | 6695.6907 | 1007 | 666.9545 | 109.4885 | 776.443 | 152.8041 | 25.0846 | 177.8887
1.0183 | CS-G34 | 865.2 | 3790.5809 | 881 | 2583.2853 | 525.8327 | 3109.1179 | 703.5647 | 143.2119 | 846.7767
1.0406 | CV-G65 | 324.8 | 1591.3473 | 338 | 1154.8319 | 133.3964 | 1288.2283 | 299.446 | 34.5895 | 334.0355 | 90.5944
1.0225 | DM-G6 | 1871.8 | 12853.597 | 1914 | 9552.5609 | 1127.1129 | 10679.6738 | 2530.451 | 298.5696 | 2829.0206
1.0036 | EL-G40 | 1009.4 | 7453.0868 | 1013 | 2979.4918 | 513.8244 | 3493.3162 | 809.3607 | 139.5773 | 948.938 | 2184.0293
1.0093 | SB-G91 | 1177 | 7182.3028 | 1188 | 2272.7151 | 572.3698 | 2845.0849 | 629.6012 | 158.5613 | 788.1625
0.97309 | SH-G35 | 1315.4 | 7287.4563 | 1280 | 992.9034 | 152.0663 | 1144.9697 | 181.7806 | 27.8403 | 209.6209
1.0099 | TH-G16 | 1111 | 5129.2871 | 1122 | 3608.1206 | 608.8703 | 4216.9909 | 932.0269 | 157.2795 | 1089.3065
| Totals | 10756.4 | 60347.4806 | 10254 | 29249.0982 | 4598.3029 | 33847.4011 | 7691.7164 | 1213.3195 | 8905.0359
>> below are the feeders supplied by feeder backup that are not in the FY27 T&D Resilience Project list but are impacted
| EJ-G7 | 2660.4 | 23207.4 | [6 empty] | 3409.357 | 832.4652
| EL-G41 | 713 | 2028.6 | [7 empty] | 1151.1994
| BE-G29 | 1763.8 | 6758.8 | [7 empty] | 554.5926
Data provided by GMP. Calculating the % of outages that occur at the feeder breaker protective device for feeder backups.
Total Customer Outages on feeder
| Feeder | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Total
| BE-G29 | 2915 | 23724 | 8078 | 808 | 35525
| BV-G44 | 10412 | 2459 | 4986 | 355 | 18212
| CS-G34 | 884 | 16051 | 1529 | 273 | 18737
| CV-G65 | 1029 | 3724 | 2211 | 273 | 7237
| EJ-G7 | 27258 | 69791 | 13882 | 704 | 111635
| EL-G40 | 13351 | 7527 | 8883 | 246 | 30007
| EL-G41 | 5735 | 1548 | 2806 | 17 | 10106
Total Customer Outages on feeder, filtered for outages at the feeder breaker protective device
| Feeder | Zone 1 | Zone 2 | Zone 3 | Zone 4 | %
| BE-G29 | 2915 |  | 0 |  | 8.205%
| BV-G44 | 10412 |  |  | 2 | 57.17%
| CS-G34 |  |  | 86 |  | 0%
| CV-G65 | 1029 |  |  |  | 14.22%
| EJ-G7 | 27258 |  |  | 0 | 24.42%
| EL-G40 | 13351 | 0 | 0 | 0 | 44.49%
| EL-G41 | 5735 | 618 | 0 |  | 56.75%
Weighted average EJ-G7 ratio by line mile treated
| Project Type | % of line miles treated in prior years |  | Applicability Score | Effectiveness Score | Combined post-mitigation score | Pre FY26 SAIFI (source, GMP 2025 R.4900 Report 40-worst Circuit list) | Post FY26 SAIFI
| OH | 40.31% |  | 80.33% | 90% | 27.7%
| UG | 59.69% |  | 83.36% | 98% | 18.31%
| Weighted Average |  |  |  |  | 22.1% | 5.8 | 1.2815 | << Conservative, circuit wide applied to feeder backup
Note on K17: Andy Eiden: Adjusting the EJ-G7 remaining outages for feeder backup by ratio of estimated post FY26 projects to baseline outage data.
Note on L17: Andy Eiden: For EJ-G7 we are only capturing the remaining the post-mitigation expected annual outages.
Note on G24: Andy Eiden: Note this table is 5-yr total outages. Only used for % of outages at feeder breaker in Zone 1.

## Outage by Zone inputs
Total Universe of Historical Average Annual Outages (pre-mitigation) By Zone
Feeder | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Total
BV-G43 | 2270.4094 | 150.1172 | 698.7275 | 60.2743 | 3179.5285
BV-G44 | 2964.0945 | 700.0296 | 1419.4175 | 101.0616 | 5184.6032
CH-G11 | 4381.6337 | 680.6318 | 1552.886 | 80.5392 | 6695.6907
CS-G34 | 2954.4561 | 471.572 | 309.3237 | 55.2292 | 3790.5809
CV-G65 | 1045.1394 | 0 | 486.1778 | 60.0301 | 1591.3473
DM-G6 | 6701.4164 | 1913.5336 | 4129.4476 | 109.1994 | 12853.597
EL-G40 | 3316.0983 | 2910.745 | 1165.1425 | 61.1011 | 7453.0868
SB-G91 | 3824.4385 | 2426.4116 | 837.3466 | 94.1061 | 7182.3028
SH-G35 | 4514.3627 | 308.2371 | 2289.9393 | 174.9173 | 7287.4563
TH-G16 | 2566.7715 | 810.2732 | 1679.8924 | 72.35 | 5129.2871
Total Customer Outages - Counts By Zone - 2020 to 2024 (Source: GMP Data)
Feeder | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Total
BV-G43 | 9982 | 660 | 3072 | 265 | 13979
BV-G44 | 10412 | 2459 | 4986 | 355 | 18212
CH-G11 | 28834 | 4479 | 10219 | 530 | 44062
CS-G34 | 14604 | 2331 | 1529 | 273 | 18737
CV-G65 | 4753 | 0 | 2211 | 273 | 7237
DM-G6 | 28966 | 8271 | 17849 | 472 | 55558
EL-G40 | 13351 | 11719 | 4691 | 246 | 30007
SB-G91 | 13533 | 8586 | 2963 | 333 | 25415
SH-G35 | 21705 | 1482 | 11010 | 841 | 35038
TH-G16 | 10856 | 3427 | 7105 | 306 | 21694
Total | 156996 | 43414 | 65635 | 3894 | 269939
Percent Total Customer Outages by Zone
Feeder | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Total
BV-G43 | 71.41% | 4.721% | 21.98% | 1.896% | 100%
BV-G44 | 57.17% | 13.5% | 27.38% | 1.949% | 100%
CH-G11 | 65.44% | 10.17% | 23.19% | 1.203% | 100%
CS-G34 | 77.94% | 12.44% | 8.16% | 1.457% | 100%
CV-G65 | 65.68% | 0% | 30.55% | 3.772% | 100%
DM-G6 | 52.14% | 14.89% | 32.13% | 0.8496% | 100%
EL-G40 | 44.49% | 39.05% | 15.63% | 0.8198% | 100%
SB-G91 | 53.25% | 33.78% | 11.66% | 1.31% | 100%
SH-G35 | 61.95% | 4.23% | 31.42% | 2.4% | 100%
TH-G16 | 50.04% | 15.8% | 32.75% | 1.411% | 100%
Total | 58.16% | 16.08% | 24.31% | 1.443% | 100%
Incident-level data for non-storm restoration cost input
Count of INCIDENT_ID by Year (Source: Provided by GMP)
FEEDER_ID | 2020 | 2021 | 2022 | 2023 | 2024 | AVG 2020-2024
BV-G43 | 36 | 34 | 64 | 78 | 57 | 53.8
BV-G44 | 82 | 73 | 68 | 92 | 75 | 78
CH-G11 | 125 | 162 | 167 | 210 | 138 | 160.4
CS-G34 | 42 | 41 | 64 | 55 | 62 | 52.8
CV-G65 | 41 | 46 | 38 | 57 | 30 | 42.4
DM-G6 | 207 | 225 | 186 | 301 | 203 | 224.4
EL-G40 | 90 | 46 | 101 | 88 | 77 | 80.4
SB-G91 | 39 | 64 | 55 | 69 | 79 | 61.2
SH-G35 | 115 | 118 | 174 | 161 | 163 | 146.2
TH-G16 | 80 | 66 | 121 | 69 | 79 | 83
Total Average Number of Incidents by Zone - Used for Avg Non-storm restoration cost per incident
FEEDER_ID | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Total | QC sumcheck
BV-G43 | 38.417 | 2.5401 | 11.823 | 1.0199 | 53.8 | 0
BV-G44 | 44.5935 | 10.5316 | 21.3545 | 1.5204 | 78 | 0
CH-G11 | 41.7946 | 79.4756 | 37.2005 | 1.9294 | 160.4 | 0
CS-G34 | 2.4911 | 45.231 | 4.3087 | 0.7693 | 52.8 | 0
CV-G65 | 6.0287 | 21.8181 | 12.9538 | 1.5994 | 42.4 | 0
DM-G6 | 46.6992 | 103.7019 | 72.0925 | 1.9064 | 224.4 | 0
EL-G40 | 35.7723 | 20.1677 | 23.8009 | 0.65913 | 80.4 | 0
SB-G91 | 32.5878 | 20.6753 | 7.135 | 0.80187 | 61.2 | 0
SH-G35 | 90.5666 | 6.1838 | 45.9405 | 3.5092 | 146.2 | 0
TH-G16 | 41.5344 | 13.1115 | 27.1833 | 1.1707 | 83 | 0
Zonal-level percent of incidents by zone (provided by GMP) (average 2020-2024)
Feeder | Zone 1 | Zone 2 | Zone 3 | Zone 4 | Total
BV-G43 | 71.41% | 4.721% | 21.98% | 1.896% | 100%
BV-G44 | 57.17% | 13.5% | 27.38% | 1.949% | 100%
CH-G11 | 26.06% | 49.55% | 23.19% | 1.203% | 100%
CS-G34 | 4.718% | 85.66% | 8.16% | 1.457% | 100%
CV-G65 | 14.22% | 51.46% | 30.55% | 3.772% | 100%
DM-G6 | 20.81% | 46.21% | 32.13% | 0.8496% | 100%
EL-G40 | 44.49% | 25.08% | 29.6% | 0.8198% | 100%
SB-G91 | 53.25% | 33.78% | 11.66% | 1.31% | 100%
SH-G35 | 61.95% | 4.23% | 31.42% | 2.4% | 100%
TH-G16 | 50.04% | 15.8% | 32.75% | 1.411% | 100%

## Storm restoration costs
Source: Data provided by GMP
Total annual storm restoration costs - Major and Minor Storms - (2025$) by FY
| Row Labels | Sum of Total Storm Costs
2015 | FY2015 | 27537114.861
2016 | FY2016 | 11697637.9606
2017 | FY2017 | 12386807.8027
2018 | FY2018 | 26496658.9734
2019 | FY2019 | 21906251.8619
2020 | FY2020 | 18304389.0595
2021 | FY2021 | 8040813.407
2022 | FY2022 | 10879927.1247
2023 | FY2023 | 57052868.6846
2024 | FY2024 | 48476310.3235
| Avg | 24277878.0059
| Slope | 2663245.8869

## Loss Reduction Calculation
STEP 1:
Average MWh/yr/mile loss reduction by project type to apply to rest of projects (source: Provided by GMP based on power flow modeling)
Project Type - Phase | Avg MWh/yr/mile |  |  |  |  | Energy price forecast (LMP) $/MWh, Source: Provided by GMP
3-Phase OH | 14.987 |  |  |  |  | Year | Month | On-Peak (adjusted for inflation) | Off-Peak (Adjusted for inflation)
1-Phase URD | 3.464 |  |  |  |  | 2024 | 2024-06-01 | 47.5 | 35.6
1-Phase OH | 0.28648 |  |  |  |  | 2024 | 2024-07-01 | 72.15 | 47.25
[6 empty] | 2024 | 2024-08-01 | 59.15 | 38.05
STEP 2: Develop average $/MWh for avoided energy losses from upgraded line capacity | [5 empty] | 2024 | 2024-09-01 | 46 | 34.4
Year | On-peak | Off-Peak | Average | Levelized | NPV | 2024 | 2024-10-01 | 44.5 | 32.85
2027 | 67.1375 | 53.7208 | 60.4292 | 71.7846 | 951.6225 | 2024 | 2024-11-01 | 67 | 58.85
2028 | 65.2664 | 54.422 | 59.8442 |  |  | 2024 | 2024-12-01 | 113.75 | 103.1
2029 | 66.2224 | 55.4378 | 60.8301 |  |  | 2025 | 2025-01-01 | 111.75 | 102
2030 | 65.2484 | 54.3047 | 59.7766 |  |  | 2025 | 2025-02-01 | 101.5 | 91.5
2031 | 66.1915 | 54.9767 | 60.5841 |  |  | 2025 | 2025-03-01 | 59 | 51
2032 | 68.4814 | 55.9859 | 62.2337 |  |  | 2025 | 2025-04-01 | 46.25 | 38
2033 | 69.7213 | 57.3834 | 63.5523 |  |  | 2025 | 2025-05-01 | 41.75 | 35
2034 | 71.1158 | 58.531 | 64.8234 |  |  | 2025 | 2025-06-01 | 51.5 | 38.75
2035 | 72.5381 | 59.7016 | 66.1199 |  |  | 2025 | 2025-07-01 | 71.25 | 47.25
2036 | 73.9888 | 60.8957 | 67.4423 |  |  | 2025 | 2025-08-01 | 63 | 42
2037 | 75.4686 | 62.1136 | 68.7911 |  |  | 2025 | 2025-09-01 | 49 | 36.5
2038 | 76.978 | 63.3559 | 70.1669 |  |  | 2025 | 2025-10-01 | 43.75 | 35.75
2039 | 78.5175 | 64.623 | 71.5703 |  |  | 2025 | 2025-11-01 | 60.5 | 53
2040 | 80.0879 | 65.9154 | 73.0017 |  |  | 2025 | 2025-12-01 | 91.5 | 81.75
2041 | 81.6897 | 67.2337 | 74.4617 |  |  | 2026 | 2026-01-01 | 133 | 121.45
2042 | 83.3234 | 68.5784 | 75.9509 |  |  | 2026 | 2026-02-01 | 112.5 | 103.7
2043 | 84.9899 | 69.95 | 77.47 |  |  | 2026 | 2026-03-01 | 65.5 | 58.15
2044 | 86.6897 | 71.349 | 79.0194 |  |  | 2026 | 2026-04-01 | 47.35 | 38.25
2045 | 88.4235 | 72.776 | 80.5997 |  |  | 2026 | 2026-05-01 | 40.5 | 32.15
2046 | 90.192 | 74.2315 | 82.2117 |  |  | 2026 | 2026-06-01 | 51.5 | 37.15
2047 | 91.9958 | 75.7161 | 83.856 |  |  | 2026 | 2026-07-01 | 72.5 | 48.75
2048 | 93.8357 | 77.2304 | 85.5331 |  |  | 2026 | 2026-08-01 | 62 | 38.5
2049 | 95.7124 | 78.7751 | 87.2437 |  |  | 2026 | 2026-09-01 | 48.25 | 35.15
2050 | 97.6267 | 80.3506 | 88.9886 |  |  | 2026 | 2026-10-01 | 44 | 34.5
2051 | 99.5792 | 81.9576 | 90.7684 |  |  | 2026 | 2026-11-01 | 57.9 | 50.9
2052 | 101.5708 | 83.5967 | 92.5838 |  |  | 2026 | 2026-12-01 | 86.65 | 75.9
2053 | 103.6022 | 85.2686 | 94.4354 |  |  | 2027 | 2027-01-01 | 132.25 | 122.25
2054 | 105.6743 | 86.974 | 96.3241 |  |  | 2027 | 2027-02-01 | 111.75 | 101.75
2055 | 107.7878 | 88.7135 | 98.2506 |  |  | 2027 | 2027-03-01 | 65 | 57
2056 | 109.9435 | 90.4878 | 100.2156 |  |  | 2027 | 2027-04-01 | 45.85 | 35.35
2057 | 112.1424 | 92.2975 | 102.22 |  |  | 2027 | 2027-05-01 | 39 | 27.5
2058 | 114.3852 | 94.1435 | 104.2644 |  |  | 2027 | 2027-06-01 | 50 | 35.25
[6 empty] | 2027 | 2027-07-01 | 71 | 46.25
STEP 3: Apply to each project based on line miles | [5 empty] | 2027 | 2027-08-01 | 60.5 | 35.75
<<happens in Mitigation Projects and Baseline Projects tab calcs>> | [5 empty] | 2027 | 2027-09-01 | 46.75 | 33.75
[6 empty] | 2027 | 2027-10-01 | 42.5 | 29.75
[6 empty] | 2027 | 2027-11-01 | 56.15 | 46.15
[6 empty] | 2027 | 2027-12-01 | 84.9 | 73.9
[6 empty] | 2028 | 2028-01-01 | 145.9509 | 119.0085
[6 empty] | 2028 | 2028-02-01 | 137.2377 | 110.4582
[6 empty] | 2028 | 2028-03-01 | 54.7561 | 48.303
[6 empty] | 2028 | 2028-04-01 | 38.8961 | 33.0811
[6 empty] | 2028 | 2028-05-01 | 34.8659 | 29.0568
[6 empty] | 2028 | 2028-06-01 | 38.5913 | 31.3981
[6 empty] | 2028 | 2028-07-01 | 47.8253 | 36.086
[6 empty] | 2028 | 2028-08-01 | 42.5277 | 35.6189
[6 empty] | 2028 | 2028-09-01 | 36.4564 | 30.7001
[6 empty] | 2028 | 2028-10-01 | 36.9606 | 31.5866
[6 empty] | 2028 | 2028-11-01 | 58.9131 | 51.642
[6 empty] | 2028 | 2028-12-01 | 110.2156 | 96.1243
[6 empty] | 2029 | 2029-01-01 | 149.7754 | 122.9478
[6 empty] | 2029 | 2029-02-01 | 143.3573 | 117.4303
[6 empty] | 2029 | 2029-03-01 | 58.0268 | 50.7853
[6 empty] | 2029 | 2029-04-01 | 38.6319 | 32.5918
[6 empty] | 2029 | 2029-05-01 | 33.7223 | 28.3075
[6 empty] | 2029 | 2029-06-01 | 37.8343 | 31.1432
[6 empty] | 2029 | 2029-07-01 | 44.1401 | 33.2895
[6 empty] | 2029 | 2029-08-01 | 41.1567 | 34.1957
[6 empty] | 2029 | 2029-09-01 | 35.0836 | 29.7344
[6 empty] | 2029 | 2029-10-01 | 35.7695 | 30.0961
[6 empty] | 2029 | 2029-11-01 | 63.3158 | 54.8909
[6 empty] | 2029 | 2029-12-01 | 113.8551 | 99.8414
[6 empty] | 2030 | 2030-01-01 | 148.442 | 121.3325
[6 empty] | 2030 | 2030-02-01 | 138.7093 | 112.8742
[6 empty] | 2030 | 2030-03-01 | 56.4521 | 49.5226
[6 empty] | 2030 | 2030-04-01 | 38.3737 | 32.7545
[6 empty] | 2030 | 2030-05-01 | 33.5687 | 27.8587
[6 empty] | 2030 | 2030-06-01 | 38.3329 | 31.1473
[6 empty] | 2030 | 2030-07-01 | 43.1022 | 32.7925
[6 empty] | 2030 | 2030-08-01 | 40.7559 | 33.977
[6 empty] | 2030 | 2030-09-01 | 34.2158 | 29.291
[6 empty] | 2030 | 2030-10-01 | 34.9763 | 28.9729
[6 empty] | 2030 | 2030-11-01 | 61.7682 | 54.6096
[6 empty] | 2030 | 2030-12-01 | 114.284 | 96.5242
[6 empty] | 2031 | 2031-01-01 | 148.4516 | 119.6577
[6 empty] | 2031 | 2031-02-01 | 139.7092 | 115.0317
[6 empty] | 2031 | 2031-03-01 | 58.5702 | 51.1754
[6 empty] | 2031 | 2031-04-01 | 37.9406 | 32.3204
[6 empty] | 2031 | 2031-05-01 | 33.6202 | 28.2278
[6 empty] | 2031 | 2031-06-01 | 39.1256 | 31.8129
[6 empty] | 2031 | 2031-07-01 | 43.5998 | 33.5874
[6 empty] | 2031 | 2031-08-01 | 43.2833 | 35.4226
[6 empty] | 2031 | 2031-09-01 | 35.6982 | 29.8513
[6 empty] | 2031 | 2031-10-01 | 36.4724 | 29.9524
[6 empty] | 2031 | 2031-11-01 | 63.4349 | 55.7468
[6 empty] | 2031 | 2031-12-01 | 114.3918 | 96.9338
[6 empty] | 2032 | 2032-01-01 | 149.578 | 119.5945
[6 empty] | 2032 | 2032-02-01 | 144.1163 | 114.3126
[6 empty] | 2032 | 2032-03-01 | 58.042 | 50.6092
[6 empty] | 2032 | 2032-04-01 | 39.3368 | 32.9909
[6 empty] | 2032 | 2032-05-01 | 33.9681 | 28.3527
[6 empty] | 2032 | 2032-06-01 | 39.1548 | 32.6471
[6 empty] | 2032 | 2032-07-01 | 46.3669 | 36.1874
[6 empty] | 2032 | 2032-08-01 | 47.2939 | 38.0844
[6 empty] | 2032 | 2032-09-01 | 38.6768 | 32.8468
[6 empty] | 2032 | 2032-10-01 | 40.0782 | 32.4101
[6 empty] | 2032 | 2032-11-01 | 65.3468 | 58.1601
[6 empty] | 2032 | 2032-12-01 | 119.8189 | 95.6345
[6 empty] | 2033 | 2033-01-01 | 154.5637 | 122.7789
[6 empty] | 2033 | 2033-02-01 | 144.0519 | 115.3126
[6 empty] | 2033 | 2033-03-01 | 59.7594 | 52.0011
[6 empty] | 2033 | 2033-04-01 | 39.8493 | 33.616
[6 empty] | 2033 | 2033-05-01 | 32.5029 | 27.725
[6 empty] | 2033 | 2033-06-01 | 39.757 | 33.3984
[6 empty] | 2033 | 2033-07-01 | 48.2773 | 38.2809
[6 empty] | 2033 | 2033-08-01 | 48.7177 | 38.6573
[6 empty] | 2033 | 2033-09-01 | 39.4958 | 34.0171
[6 empty] | 2033 | 2033-10-01 | 43.1201 | 34.5699
[6 empty] | 2033 | 2033-11-01 | 67.1266 | 58.6492
[6 empty] | 2033 | 2033-12-01 | 119.4343 | 99.5938
[6 empty] | 2034 | 2034-01-01 | 157.655 | 125.2345
[6 empty] | 2034 | 2034-02-01 | 146.9329 | 117.6189
[6 empty] | 2034 | 2034-03-01 | 60.9546 | 53.0411
[6 empty] | 2034 | 2034-04-01 | 40.6463 | 34.2884
[6 empty] | 2034 | 2034-05-01 | 33.153 | 28.2795
[6 empty] | 2034 | 2034-06-01 | 40.5522 | 34.0664
[6 empty] | 2034 | 2034-07-01 | 49.2428 | 39.0465
[6 empty] | 2034 | 2034-08-01 | 49.6921 | 39.4304
[6 empty] | 2034 | 2034-09-01 | 40.2857 | 34.6974
[6 empty] | 2034 | 2034-10-01 | 43.9825 | 35.2613
[6 empty] | 2034 | 2034-11-01 | 68.4691 | 59.8222
[6 empty] | 2034 | 2034-12-01 | 121.823 | 101.5857
[6 empty] | 2035 | 2035-01-01 | 160.8081 | 127.7391
[6 empty] | 2035 | 2035-02-01 | 149.8716 | 119.9712
[6 empty] | 2035 | 2035-03-01 | 62.1737 | 54.102
[6 empty] | 2035 | 2035-04-01 | 41.4592 | 34.9741
[6 empty] | 2035 | 2035-05-01 | 33.8161 | 28.8451
[6 empty] | 2035 | 2035-06-01 | 41.3632 | 34.7477
[6 empty] | 2035 | 2035-07-01 | 50.2277 | 39.8275
[6 empty] | 2035 | 2035-08-01 | 50.6859 | 40.219
[6 empty] | 2035 | 2035-09-01 | 41.0914 | 35.3914
[6 empty] | 2035 | 2035-10-01 | 44.8621 | 35.9666
[6 empty] | 2035 | 2035-11-01 | 69.8385 | 61.0186
[6 empty] | 2035 | 2035-12-01 | 124.2595 | 103.6174
[6 empty] | 2036 | 2036-01-01 | 164.0243 | 130.2939
[6 empty] | 2036 | 2036-02-01 | 152.869 | 122.3707
[6 empty] | 2036 | 2036-03-01 | 63.4171 | 55.184
[6 empty] | 2036 | 2036-04-01 | 42.2884 | 35.6736
[6 empty] | 2036 | 2036-05-01 | 34.4924 | 29.422
[6 empty] | 2036 | 2036-06-01 | 42.1905 | 35.4427
[6 empty] | 2036 | 2036-07-01 | 51.2322 | 40.624
[6 empty] | 2036 | 2036-08-01 | 51.6996 | 41.0234
[6 empty] | 2036 | 2036-09-01 | 41.9132 | 36.0992
[6 empty] | 2036 | 2036-10-01 | 45.7594 | 36.6859
[6 empty] | 2036 | 2036-11-01 | 71.2352 | 62.239
[6 empty] | 2036 | 2036-12-01 | 126.7447 | 105.6898
[6 empty] | 2037 | 2037-01-01 | 167.3048 | 132.8998
[6 empty] | 2037 | 2037-02-01 | 155.9264 | 124.8181
[6 empty] | 2037 | 2037-03-01 | 64.6855 | 56.2877
[6 empty] | 2037 | 2037-04-01 | 43.1342 | 36.3871
[6 empty] | 2037 | 2037-05-01 | 35.1822 | 30.0104
[6 empty] | 2037 | 2037-06-01 | 43.0343 | 36.1515
[6 empty] | 2037 | 2037-07-01 | 52.2569 | 41.4365
[6 empty] | 2037 | 2037-08-01 | 52.7336 | 41.8439
[6 empty] | 2037 | 2037-09-01 | 42.7515 | 36.8212
[6 empty] | 2037 | 2037-10-01 | 46.6745 | 37.4196
[6 empty] | 2037 | 2037-11-01 | 72.66 | 63.4837
[6 empty] | 2037 | 2037-12-01 | 129.2796 | 107.8036
[6 empty] | 2038 | 2038-01-01 | 170.6508 | 135.5578
[6 empty] | 2038 | 2038-02-01 | 159.0449 | 127.3144
[6 empty] | 2038 | 2038-03-01 | 65.9792 | 57.4134
[6 empty] | 2038 | 2038-04-01 | 43.9969 | 37.1148
[6 empty] | 2038 | 2038-05-01 | 35.8859 | 30.6106
[6 empty] | 2038 | 2038-06-01 | 43.895 | 36.8746
[6 empty] | 2038 | 2038-07-01 | 53.302 | 42.2652
[6 empty] | 2038 | 2038-08-01 | 53.7883 | 42.6808
[6 empty] | 2038 | 2038-09-01 | 43.6065 | 37.5576
[6 empty] | 2038 | 2038-10-01 | 47.608 | 38.168
[6 empty] | 2038 | 2038-11-01 | 74.1132 | 64.7534
[6 empty] | 2038 | 2038-12-01 | 131.8652 | 109.9596
[6 empty] | 2039 | 2039-01-01 | 174.0639 | 138.269
[6 empty] | 2039 | 2039-02-01 | 162.2258 | 129.8607
[6 empty] | 2039 | 2039-03-01 | 67.2988 | 58.5617
[6 empty] | 2039 | 2039-04-01 | 44.8768 | 37.8571
[6 empty] | 2039 | 2039-05-01 | 36.6036 | 31.2228
[6 empty] | 2039 | 2039-06-01 | 44.7729 | 37.6121
[6 empty] | 2039 | 2039-07-01 | 54.368 | 43.1105
[6 empty] | 2039 | 2039-08-01 | 54.8641 | 43.5344
[6 empty] | 2039 | 2039-09-01 | 44.4786 | 38.3088
[6 empty] | 2039 | 2039-10-01 | 48.5602 | 38.9314
[6 empty] | 2039 | 2039-11-01 | 75.5954 | 66.0485
[6 empty] | 2039 | 2039-12-01 | 134.5025 | 112.1588
[6 empty] | 2040 | 2040-01-01 | 177.5451 | 141.0343
[6 empty] | 2040 | 2040-02-01 | 165.4703 | 132.4579
[6 empty] | 2040 | 2040-03-01 | 68.6447 | 59.7329
[6 empty] | 2040 | 2040-04-01 | 45.7743 | 38.6143
[6 empty] | 2040 | 2040-05-01 | 37.3357 | 31.8473
[6 empty] | 2040 | 2040-06-01 | 45.6683 | 38.3643
[6 empty] | 2040 | 2040-07-01 | 55.4554 | 43.9727
[6 empty] | 2040 | 2040-08-01 | 55.9614 | 44.4051
[6 empty] | 2040 | 2040-09-01 | 45.3682 | 39.0749
[6 empty] | 2040 | 2040-10-01 | 49.5314 | 39.71
[6 empty] | 2040 | 2040-11-01 | 77.1073 | 67.3695
[6 empty] | 2040 | 2040-12-01 | 137.1925 | 114.402
[6 empty] | 2041 | 2041-01-01 | 181.096 | 143.855
[6 empty] | 2041 | 2041-02-01 | 168.7798 | 135.1071
[6 empty] | 2041 | 2041-03-01 | 70.0176 | 60.9276
[6 empty] | 2041 | 2041-04-01 | 46.6898 | 39.3866
[6 empty] | 2041 | 2041-05-01 | 38.0824 | 32.4842
[6 empty] | 2041 | 2041-06-01 | 46.5817 | 39.1316
[6 empty] | 2041 | 2041-07-01 | 56.5645 | 44.8522
[6 empty] | 2041 | 2041-08-01 | 57.0806 | 45.2932
[6 empty] | 2041 | 2041-09-01 | 46.2756 | 39.8564
[6 empty] | 2041 | 2041-10-01 | 50.522 | 40.5042
[6 empty] | 2041 | 2041-11-01 | 78.6495 | 68.7169
[6 empty] | 2041 | 2041-12-01 | 139.9364 | 116.69
[6 empty] | 2042 | 2042-01-01 | 184.718 | 146.7321
[6 empty] | 2042 | 2042-02-01 | 172.1554 | 137.8092
[6 empty] | 2042 | 2042-03-01 | 71.418 | 62.1462
[6 empty] | 2042 | 2042-04-01 | 47.6236 | 40.1743
[6 empty] | 2042 | 2042-05-01 | 38.844 | 33.1339
[6 empty] | 2042 | 2042-06-01 | 47.5133 | 39.9142
[6 empty] | 2042 | 2042-07-01 | 57.6958 | 45.7492
[6 empty] | 2042 | 2042-08-01 | 58.2222 | 46.199
[6 empty] | 2042 | 2042-09-01 | 47.2011 | 40.6536
[6 empty] | 2042 | 2042-10-01 | 51.5325 | 41.3143
[6 empty] | 2042 | 2042-11-01 | 80.2225 | 70.0912
[6 empty] | 2042 | 2042-12-01 | 142.7351 | 119.0238
[6 empty] | 2043 | 2043-01-01 | 188.4123 | 149.6668
[6 empty] | 2043 | 2043-02-01 | 175.5985 | 140.5654
[6 empty] | 2043 | 2043-03-01 | 72.8463 | 63.3891
[6 empty] | 2043 | 2043-04-01 | 48.5761 | 40.9778
[6 empty] | 2043 | 2043-05-01 | 39.6209 | 33.7966
[6 empty] | 2043 | 2043-06-01 | 48.4636 | 40.7125
[6 empty] | 2043 | 2043-07-01 | 58.8497 | 46.6642
[6 empty] | 2043 | 2043-08-01 | 59.3866 | 47.123
[6 empty] | 2043 | 2043-09-01 | 48.1451 | 41.4666
[6 empty] | 2043 | 2043-10-01 | 52.5631 | 42.1406
[6 empty] | 2043 | 2043-11-01 | 81.8269 | 71.493
[6 empty] | 2043 | 2043-12-01 | 145.5898 | 121.4043
[6 empty] | 2044 | 2044-01-01 | 192.1806 | 152.6601
[6 empty] | 2044 | 2044-02-01 | 179.1104 | 143.3767
[6 empty] | 2044 | 2044-03-01 | 74.3033 | 64.6569
[6 empty] | 2044 | 2044-04-01 | 49.5476 | 41.7973
[6 empty] | 2044 | 2044-05-01 | 40.4133 | 34.4725
[6 empty] | 2044 | 2044-06-01 | 49.4329 | 41.5268
[6 empty] | 2044 | 2044-07-01 | 60.0267 | 47.5975
[6 empty] | 2044 | 2044-08-01 | 60.5744 | 48.0655
[6 empty] | 2044 | 2044-09-01 | 49.108 | 42.296
[6 empty] | 2044 | 2044-10-01 | 53.6144 | 42.9834
[6 empty] | 2044 | 2044-11-01 | 83.4634 | 72.9229
[6 empty] | 2044 | 2044-12-01 | 148.5016 | 123.8324
[6 empty] | 2045 | 2045-01-01 | 196.0242 | 155.7133
[6 empty] | 2045 | 2045-02-01 | 182.6926 | 146.2443
[6 empty] | 2045 | 2045-03-01 | 75.7893 | 65.95
[6 empty] | 2045 | 2045-04-01 | 50.5386 | 42.6333
[6 empty] | 2045 | 2045-05-01 | 41.2216 | 35.162
[6 empty] | 2045 | 2045-06-01 | 50.4215 | 42.3573
[6 empty] | 2045 | 2045-07-01 | 61.2272 | 48.5494
[6 empty] | 2045 | 2045-08-01 | 61.7859 | 49.0268
[6 empty] | 2045 | 2045-09-01 | 50.0902 | 43.1419
[6 empty] | 2045 | 2045-10-01 | 54.6867 | 43.843
[6 empty] | 2045 | 2045-11-01 | 85.1327 | 74.3813
[6 empty] | 2045 | 2045-12-01 | 151.4716 | 126.3091
[6 empty] | 2046 | 2046-01-01 | 199.9447 | 158.8276
[6 empty] | 2046 | 2046-02-01 | 186.3465 | 149.1692
[6 empty] | 2046 | 2046-03-01 | 77.3051 | 67.269
[6 empty] | 2046 | 2046-04-01 | 51.5493 | 43.4859
[6 empty] | 2046 | 2046-05-01 | 42.046 | 35.8652
[6 empty] | 2046 | 2046-06-01 | 51.43 | 43.2044
[6 empty] | 2046 | 2046-07-01 | 62.4518 | 49.5204
[6 empty] | 2046 | 2046-08-01 | 63.0216 | 50.0073
[6 empty] | 2046 | 2046-09-01 | 51.092 | 44.0047
[6 empty] | 2046 | 2046-10-01 | 55.7804 | 44.7199
[6 empty] | 2046 | 2046-11-01 | 86.8354 | 75.869
[6 empty] | 2046 | 2046-12-01 | 154.501 | 128.8352
[6 empty] | 2047 | 2047-01-01 | 203.9436 | 162.0041
[6 empty] | 2047 | 2047-02-01 | 190.0734 | 152.1525
[6 empty] | 2047 | 2047-03-01 | 78.8512 | 68.6144
[6 empty] | 2047 | 2047-04-01 | 52.5803 | 44.3557
[6 empty] | 2047 | 2047-05-01 | 42.8869 | 36.5825
[6 empty] | 2047 | 2047-06-01 | 52.4586 | 44.0685
[6 empty] | 2047 | 2047-07-01 | 63.7008 | 50.5108
[6 empty] | 2047 | 2047-08-01 | 64.282 | 51.0075
[6 empty] | 2047 | 2047-09-01 | 52.1138 | 44.8848
[6 empty] | 2047 | 2047-10-01 | 56.896 | 45.6143
[6 empty] | 2047 | 2047-11-01 | 88.5721 | 77.3863
[6 empty] | 2047 | 2047-12-01 | 157.5911 | 131.4119
[6 empty] | 2048 | 2048-01-01 | 208.0224 | 165.2442
[6 empty] | 2048 | 2048-02-01 | 193.8749 | 155.1956
[6 empty] | 2048 | 2048-03-01 | 80.4282 | 69.9867
[6 empty] | 2048 | 2048-04-01 | 53.6319 | 45.2428
[6 empty] | 2048 | 2048-05-01 | 43.7447 | 37.3142
[6 empty] | 2048 | 2048-06-01 | 53.5077 | 44.9499
[6 empty] | 2048 | 2048-07-01 | 64.9748 | 51.5211
[6 empty] | 2048 | 2048-08-01 | 65.5676 | 52.0276
[6 empty] | 2048 | 2048-09-01 | 53.1561 | 45.7825
[6 empty] | 2048 | 2048-10-01 | 58.0339 | 46.5266
[6 empty] | 2048 | 2048-11-01 | 90.3435 | 78.9341
[6 empty] | 2048 | 2048-12-01 | 160.7429 | 134.0402
[6 empty] | 2049 | 2049-01-01 | 212.1829 | 168.5491
[6 empty] | 2049 | 2049-02-01 | 197.7524 | 158.2995
[6 empty] | 2049 | 2049-03-01 | 82.0368 | 71.3864
[6 empty] | 2049 | 2049-04-01 | 54.7046 | 46.1476
[6 empty] | 2049 | 2049-05-01 | 44.6196 | 38.0604
[6 empty] | 2049 | 2049-06-01 | 54.5779 | 45.8489
[6 empty] | 2049 | 2049-07-01 | 66.2743 | 52.5515
[6 empty] | 2049 | 2049-08-01 | 66.879 | 53.0682
[6 empty] | 2049 | 2049-09-01 | 54.2192 | 46.6982
[6 empty] | 2049 | 2049-10-01 | 59.1946 | 47.4571
[6 empty] | 2049 | 2049-11-01 | 92.1504 | 80.5127
[6 empty] | 2049 | 2049-12-01 | 163.9577 | 136.721
[6 empty] | 2050 | 2050-01-01 | 216.4265 | 171.9201
[6 empty] | 2050 | 2050-02-01 | 201.7074 | 161.4655
[6 empty] | 2050 | 2050-03-01 | 83.6775 | 72.8141
[6 empty] | 2050 | 2050-04-01 | 55.7987 | 47.0706
[6 empty] | 2050 | 2050-05-01 | 45.512 | 38.8216
[6 empty] | 2050 | 2050-06-01 | 55.6694 | 46.7659
[6 empty] | 2050 | 2050-07-01 | 67.5998 | 53.6025
[6 empty] | 2050 | 2050-08-01 | 68.2166 | 54.1295
[6 empty] | 2050 | 2050-09-01 | 55.3036 | 47.6321
[6 empty] | 2050 | 2050-10-01 | 60.3785 | 48.4063
[6 empty] | 2050 | 2050-11-01 | 93.9934 | 82.123
[6 empty] | 2050 | 2050-12-01 | 167.2369 | 139.4554
[6 empty] | 2051 | 2051-01-01 | 220.7551 | 175.3585
[6 empty] | 2051 | 2051-02-01 | 205.7416 | 164.6948
[6 empty] | 2051 | 2051-03-01 | 85.3511 | 74.2704
[6 empty] | 2051 | 2051-04-01 | 56.9146 | 48.012
[6 empty] | 2051 | 2051-05-01 | 46.4222 | 39.5981
[6 empty] | 2051 | 2051-06-01 | 56.7828 | 47.7012
[6 empty] | 2051 | 2051-07-01 | 68.9518 | 54.6746
[6 empty] | 2051 | 2051-08-01 | 69.5809 | 55.2121
[6 empty] | 2051 | 2051-09-01 | 56.4097 | 48.5848
[6 empty] | 2051 | 2051-10-01 | 61.5861 | 49.3744
[6 empty] | 2051 | 2051-11-01 | 95.8733 | 83.7655
[6 empty] | 2051 | 2051-12-01 | 170.5816 | 142.2445
[6 empty] | 2052 | 2052-01-01 | 225.1702 | 178.8656
[6 empty] | 2052 | 2052-02-01 | 209.8564 | 167.9887
[6 empty] | 2052 | 2052-03-01 | 87.0581 | 75.7558
[6 empty] | 2052 | 2052-04-01 | 58.0529 | 48.9722
[6 empty] | 2052 | 2052-05-01 | 47.3506 | 40.39
[6 empty] | 2052 | 2052-06-01 | 57.9185 | 48.6552
[6 empty] | 2052 | 2052-07-01 | 70.3309 | 55.768
[6 empty] | 2052 | 2052-08-01 | 70.9725 | 56.3164
[6 empty] | 2052 | 2052-09-01 | 57.5379 | 49.5565
[6 empty] | 2052 | 2052-10-01 | 62.8178 | 50.3619
[6 empty] | 2052 | 2052-11-01 | 97.7907 | 85.4408
[6 empty] | 2052 | 2052-12-01 | 173.9933 | 145.0894
[6 empty] | 2053 | 2053-01-01 | 229.6736 | 182.4429
[6 empty] | 2053 | 2053-02-01 | 214.0535 | 171.3485
[6 empty] | 2053 | 2053-03-01 | 88.7993 | 77.2709
[6 empty] | 2053 | 2053-04-01 | 59.214 | 49.9517
[6 empty] | 2053 | 2053-05-01 | 48.2977 | 41.1978
[6 empty] | 2053 | 2053-06-01 | 59.0769 | 49.6283
[6 empty] | 2053 | 2053-07-01 | 71.7375 | 56.8834
[6 empty] | 2053 | 2053-08-01 | 72.392 | 57.4427
[6 empty] | 2053 | 2053-09-01 | 58.6886 | 50.5476
[6 empty] | 2053 | 2053-10-01 | 64.0741 | 51.3691
[6 empty] | 2053 | 2053-11-01 | 99.7465 | 87.1496
[6 empty] | 2053 | 2053-12-01 | 177.4731 | 147.9912
[6 empty] | 2054 | 2054-01-01 | 234.267 | 186.0918
[6 empty] | 2054 | 2054-02-01 | 218.3346 | 174.7754
[6 empty] | 2054 | 2054-03-01 | 90.5753 | 78.8163
[6 empty] | 2054 | 2054-04-01 | 60.3983 | 50.9507
[6 empty] | 2054 | 2054-05-01 | 49.2636 | 42.0218
[6 empty] | 2054 | 2054-06-01 | 60.2584 | 50.6209
[6 empty] | 2054 | 2054-07-01 | 73.1722 | 58.0211
[6 empty] | 2054 | 2054-08-01 | 73.8398 | 58.5915
[6 empty] | 2054 | 2054-09-01 | 59.8624 | 51.5586
[6 empty] | 2054 | 2054-10-01 | 65.3556 | 52.3965
[6 empty] | 2054 | 2054-11-01 | 101.7415 | 88.8926
[6 empty] | 2054 | 2054-12-01 | 181.0226 | 150.951
[6 empty] | 2055 | 2055-01-01 | 238.9524 | 189.8136
[6 empty] | 2055 | 2055-02-01 | 222.7013 | 178.2709
[6 empty] | 2055 | 2055-03-01 | 92.3868 | 80.3927
[6 empty] | 2055 | 2055-04-01 | 61.6062 | 51.9697
[6 empty] | 2055 | 2055-05-01 | 50.2489 | 42.8622
[6 empty] | 2055 | 2055-06-01 | 61.4636 | 51.6333
[6 empty] | 2055 | 2055-07-01 | 74.6357 | 59.1815
[6 empty] | 2055 | 2055-08-01 | 75.3166 | 59.7634
[6 empty] | 2055 | 2055-09-01 | 61.0596 | 52.5897
[6 empty] | 2055 | 2055-10-01 | 66.6627 | 53.4444
[6 empty] | 2055 | 2055-11-01 | 103.7763 | 90.6704
[6 empty] | 2055 | 2055-12-01 | 184.643 | 153.97
[6 empty] | 2056 | 2056-01-01 | 243.7314 | 193.6099
[6 empty] | 2056 | 2056-02-01 | 227.1553 | 181.8364
[6 empty] | 2056 | 2056-03-01 | 94.2345 | 82.0005
[6 empty] | 2056 | 2056-04-01 | 62.8383 | 53.0091
[6 empty] | 2056 | 2056-05-01 | 51.2539 | 43.7195
[6 empty] | 2056 | 2056-06-01 | 62.6928 | 52.666
[6 empty] | 2056 | 2056-07-01 | 76.1284 | 60.3651
[6 empty] | 2056 | 2056-08-01 | 76.823 | 60.9586
[6 empty] | 2056 | 2056-09-01 | 62.2808 | 53.6415
[6 empty] | 2056 | 2056-10-01 | 67.996 | 54.5133
[6 empty] | 2056 | 2056-11-01 | 105.8518 | 92.4838
[6 empty] | 2056 | 2056-12-01 | 188.3359 | 157.0494
[6 empty] | 2057 | 2057-01-01 | 248.6061 | 197.4821
[6 empty] | 2057 | 2057-02-01 | 231.6984 | 185.4731
[6 empty] | 2057 | 2057-03-01 | 96.1192 | 83.6405
[6 empty] | 2057 | 2057-04-01 | 64.0951 | 54.0693
[6 empty] | 2057 | 2057-05-01 | 52.2789 | 44.5939
[6 empty] | 2057 | 2057-06-01 | 63.9467 | 53.7193
[6 empty] | 2057 | 2057-07-01 | 77.6509 | 61.5724
[6 empty] | 2057 | 2057-08-01 | 78.3594 | 62.1778
[6 empty] | 2057 | 2057-09-01 | 63.5264 | 54.7144
[6 empty] | 2057 | 2057-10-01 | 69.3559 | 55.6036
[6 empty] | 2057 | 2057-11-01 | 107.9689 | 94.3335
[6 empty] | 2057 | 2057-12-01 | 192.1026 | 160.1904
[6 empty] | 2058 | 2058-01-01 | 253.5782 | 201.4318
[6 empty] | 2058 | 2058-02-01 | 236.3324 | 189.1826
[6 empty] | 2058 | 2058-03-01 | 98.0416 | 85.3133
[6 empty] | 2058 | 2058-04-01 | 65.377 | 55.1507
[6 empty] | 2058 | 2058-05-01 | 53.3245 | 45.4857
[6 empty] | 2058 | 2058-06-01 | 65.2256 | 54.7937
[6 empty] | 2058 | 2058-07-01 | 79.204 | 62.8039
[6 empty] | 2058 | 2058-08-01 | 79.9266 | 63.4214
[6 empty] | 2058 | 2058-09-01 | 64.797 | 55.8086
[6 empty] | 2058 | 2058-10-01 | 70.743 | 56.7157
[6 empty] | 2058 | 2058-11-01 | 110.1282 | 96.2202
[6 empty] | 2058 | 2058-12-01 | 195.9447 | 163.3942

## ICE Inputs
Final ICE value inputs for customer resilience value | [7 empty] | Summary from ICE v2.0 National Update Study - Phase 1
Sector | Value ($/event) | [6 empty] | NON-RES | Duration | Value $/event
Residential | 21 | [7 empty] | 2 | 2839
Nonresidential | 3885 | [7 empty] | 8 | 6172
[9 empty] | 24 | 12646
[8 empty] | RES | Duration | Value $/event
Final ICE Model Run | [8 empty] | 2 | 10.49
Vermont Specific Outputs - Generated 12/12/25 with specific inputs for the target area | [8 empty] | 8 | 25.55
Website: | https://icecalculator.com/interruption-cost/results | [7 empty] | 24 | 54.52
Model Input
Version | Date | # Residential | # Non-Residential | States | SAIDI | SAIFI | CAIDI
interruption.2.1.0 | 2026-01-14 | 8802 | 1452 | Vermont | 2056 | 6 | 347
Model Outputs
Sector | # of Customers | Cost Per Customer (2023 $) Per... |  |  |  |  | Total Cost
|  | Event | Average kW | Unserved kWh | Interrupted Minutes | Annual Cost
Residential | 8802 | 21 | 26 | 5 | 0 | 122 | 1073382
Non-Residential | 1452 | 3885 | 665 | 115 | 11 | 23036 | 33448565
All | 10254 | 568 | 379 | 66 | 2 | 3367 | 34521947
Residential Cost/Event Relative To (%):
Daily Household Income | Annual Household Income
7.09% | 0.12%
Non-Residential Cost/Event Relative To (%):
Daily GDP | Annual GDP
207% | 3.36%

## BESS Full Program
Source: Provided by GMP
| Year | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33
| Monthly Customers Year 1 | 200
| Monthly Customers Year 2 |  | 100
| Monthly Customers Year 3 |  |  | 0
| Costs | [33 empty] | Lifetime NPV | per system
| Equipment & Installation Costs Year 1 | -591280.5981 | -544130.1928 | -497292.8095 | -460668.7884 | -427849.778 | -397884.5258 | -373626.7898 | -352222.812 | -331018.8341 | -309814.8562 | -288410.8783 | -267006.9004 | -245802.9226 | -224398.9447 | -202994.9668 | -181590.9889 | -3.3648e-11 | -8.0114e-12 | -8.0114e-12 | -8.0114e-12 | -8.0114e-12 | -8.0114e-12 | -8.0114e-12 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Equipment & Installation Costs Year 2 |  | -295640.299 | -272065.0964 | -248646.4047 | -230334.3942 | -213924.889 | -198942.2629 | -186813.3949 | -176111.406 | -165509.417 | -154907.4281 | -144205.4392 | -133503.4502 | -122901.4613 | -112199.4723 | -101497.4834 | -90795.4945 | -1.6824e-11 | -4.0057e-12 | -4.0057e-12 | -4.0057e-12 | -4.0057e-12 | -4.0057e-12 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Equipment & Installation Costs Year 3 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Total Equipment & Installation Costs* | -591280.5981 | -839770.4919 | -769357.9059 | -709315.1931 | -658184.1722 | -611809.4148 | -572569.0527 | -539036.2069 | -507130.24 | -475324.2732 | -443318.3064 | -411212.3396 | -379306.3728 | -347300.406 | -315194.4392 | -283088.4723 | -90795.4945 | -2.4835e-11 | -1.2017e-11 | -1.2017e-11 | -1.2017e-11 | -1.2017e-11 | -1.2017e-11 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | -5611208.4245 | -18704.0281
| O&M Cost Year 1 | -600 | -612 | -624.24 | -636.7248 | -649.4593 | -662.4485 | -675.6975 | -689.2114 | -702.9956 | -717.0555 | -724.0827 | -731.1041 | -738.1167 | -729.5941 | -720.4354 | -694.4681 | -617.7536 | -462.0797 | -257.0843 | 0
| O&M Cost Year 2 |  | -306 | -312.12 | -318.3624 | -324.7296 | -331.2242 | -337.8487 | -344.6057 | -351.4978 | -358.5278 | -365.6983 | -369.2822 | -372.8631 | -376.4395 | -372.093 | -367.4221 | -354.1787 | -315.0543 | -235.6606 | -131.113 | 0
| O&M Cost Year 3 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total O&M Costs | -600 | -918 | -936.36 | -955.0872 | -974.1889 | -993.6727 | -1013.5462 | -1033.8171 | -1054.4934 | -1075.5833 | -1089.781 | -1100.3863 | -1110.9798 | -1106.0337 | -1092.5284 | -1061.8901 | -971.9323 | -777.134 | -492.745 | -131.113 | 0 | 0 | 0 | [10 empty] | -10346.5959 | -34.4887
| Software fees Year 1 | 0 | -4800 | -4800 | -4800 | -4800 | -4800 | -4800 | -4800 | -4800 | -4800 | -4752 | -4704 | -4656 | -4512 | -4368 | -4128 | -3600 | -2640 | -1440 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Software fees Year 2 | 0 | -2400 | -2400 | -2400 | -2400 | -2400 | -2400 | -2400 | -2400 | -2400 | -2400 | -2376 | -2352 | -2328 | -2256 | -2184 | -2064 | -1800 | -1320 | -720 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Software fees Year 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Software Fees | 0 | -7200 | -7200 | -7200 | -7200 | -7200 | -7200 | -7200 | -7200 | -7200 | -7152 | -7080 | -7008 | -6840 | -6624 | -6312 | -5664 | -4440 | -2760 | -720 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | -67271.2146 | -224.2374
| FR Participation Credit Year 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FR Participation Credit Year 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FR Participation Credit Year 3 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FR Participation Credit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0
| RTE Credit Year 1 | -13489.7927 | -13759.5886 | -13760.7005 | -14035.9145 | -14316.6328 | -14602.9654 | -14601.2748 | -14893.3002 | -14888.5897 | -15186.3615 | -15028.1703 | -15022.159 | -15166.2491 | -14675.5308 | -14332.0609 | -13806.552 | -11964.4908 | -9027.4541 | -4891.2883 | 0 | 0 | 0 | 0
| RTE Credit Year 2 |  | -6879.7943 | -7017.3902 | -7017.9572 | -7158.3164 | -7301.4827 | -7447.5124 | -7446.6501 | -7595.5831 | -7593.1808 | -7745.0444 | -7664.3668 | -7661.3011 | -7734.787 | -7484.5207 | -7309.3511 | -7041.3415 | -6101.8903 | -4604.0016 | -2494.5571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RTE Credit Year 3
| RTE Credit | -13489.7927 | -20639.3829 | -20778.0907 | -21053.8717 | -21474.9492 | -21904.4482 | -22048.7871 | -22339.9504 | -22484.1729 | -22779.5423 | -22773.2146 | -22686.5258 | -22827.5502 | -22410.3179 | -21816.5817 | -21115.9031 | -19005.8323 | -15129.3444 | -9495.29 | -2494.5571 | 0 | 0 | 0
| Total Costs | -605370.3908 | -868527.8748 | -798272.3566 | -738524.152 | -687833.3103 | -641907.5357 | -602831.386 | -569609.9743 | -537868.9063 | -506379.3988 | -474333.3021 | -442079.2517 | -410252.9028 | -377656.7575 | -344727.5492 | -311578.2656 | -116437.2591 | -20346.4784 | -12748.0349 | -3345.6701 | -1.2017e-11 | -1.2017e-11 | -1.2017e-11 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Revenues
| Battery Value Year 1 | 393462.9975 | 419837.2072 | 436913.9417 | 448944.1999 | 440558.4445 | 426253.0558 | 548758.9213 | 539335.6429 | 377302.746 | 371845.6009 | 386697.0113 | 391650.8441 | 381717.5974 | 362930.616 | 342564.5668 | 316251.0945 | 270196.0818 | 202375.7739 | 117079.3925 | 21755.4478 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Battery Value Year 2 |  | 185556.8191 | 220975.0326 | 224854.4317 | 220197.6413 | 213091.8679 | 208268.227 | 270091.7251 | 264908.1112 | 186238.7594 | 196608.4546 | 199773.5779 | 193214.3059 | 187998.1992 | 177402.6591 | 166447.1146 | 153794.6647 | 131409.4073 | 98454.1447 | 56959.6077 | 10538.7239 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Battery Value Year 3 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Total Battery Value | 393462.9975 | 605394.0263 | 657888.9743 | 673798.6316 | 660756.0858 | 639344.9238 | 757027.1483 | 809427.368 | 642210.8572 | 558084.3603 | 583305.466 | 591424.4221 | 574931.9033 | 550928.8152 | 519967.2259 | 482698.2091 | 423990.7464 | 333785.1811 | 215533.5372 | 78715.0555 | 10538.7239 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 6316228.6393 | 21054.0955
| Tier 3 Value | 97000 | 48500 | 0 | [30 empty] | 133889.2665 | 446.2976
| End of life removal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -600 | -900 | -900 | -2100 | -2700 | -3900 | -8100 | -15300 | -21000 | -25500 | -9000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -28290.3838 | -94.3013
| Capitalized A&G | 285824 | 142912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Customer Payment (Upfront) | 0 | 0 | 0
| Customer/ZOI Battery Payment (monthly year 1) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer/ZOI Battery Payment (monthly year 2) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer/ZOI Battery Payment (monthly year 3) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Customer Payment (Monthly) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Revenue | 776286.9975 | 796806.0263 | 657888.9743 | 673798.6316 | 660756.0858 | 639344.9238 | 757027.1483 | 809427.368 | 642210.8572 | 558084.3603 | 582705.466 | 590524.4221 | 574031.9033 | 548828.8152 | 517267.2259 | 478798.2091 | 415890.7464 | 318485.1811 | 194533.5372 | 53215.0555 | 1538.7239 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| Net Benefit | 170916.6067 | -71721.8484 | -140383.3823 | -64725.5204 | -27077.2245 | -2562.612 | 154195.7622 | 239817.3937 | 104341.9508 | 51704.9615 | 108372.1639 | 148445.1704 | 163779.0005 | 171172.0577 | 172539.6766 | 167219.9435 | 299453.4874 | 298138.7027 | 181785.5023 | 49869.3855 | 1538.7239 | -1.2017e-11 | -1.2017e-11 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 906777.3215
487559.7431

## BESS Monthly Value (1)
Source: Provided by GMP
kW per system | 11.5
Year |  | 2026 | 2026 | 2026 | 2026 | 2026 | 2026 | 2026 | 2026 | 2026 | 2026 | 2026 | 2026 | 2027 | 2027 | 2027 | 2027 | 2027 | 2027 | 2027 | 2027 | 2027 | 2027 | 2027 | 2027 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2029 | 2029 | 2029 | 2029 | 2029 | 2029 | 2029 | 2029 | 2029 | 2029 | 2029 | 2029 | 2030 | 2030 | 2030 | 2030 | 2030 | 2030 | 2030 | 2030 | 2030 | 2030 | 2030 | 2030 | 2031 | 2031 | 2031 | 2031 | 2031 | 2031 | 2031 | 2031 | 2031 | 2031 | 2031 | 2031 | 2032 | 2032 | 2032 | 2032 | 2032 | 2032 | 2032 | 2032 | 2032 | 2032 | 2032 | 2032 | 2033 | 2033 | 2033 | 2033 | 2033 | 2033 | 2033 | 2033 | 2033 | 2033 | 2033 | 2033 | 2034 | 2034 | 2034 | 2034 | 2034 | 2034 | 2034 | 2034 | 2034 | 2034 | 2034 | 2034 | 2035 | 2035 | 2035 | 2035 | 2035 | 2035 | 2035 | 2035 | 2035 | 2035 | 2035 | 2035 | 2036 | 2036 | 2036 | 2036 | 2036 | 2036 | 2036 | 2036 | 2036 | 2036 | 2036 | 2036 | 2037 | 2037 | 2037 | 2037 | 2037 | 2037 | 2037 | 2037 | 2037 | 2037 | 2037 | 2037 | 2038 | 2038 | 2038 | 2038 | 2038 | 2038 | 2038 | 2038 | 2038 | 2038 | 2038 | 2038 | 2039 | 2039 | 2039 | 2039 | 2039 | 2039 | 2039 | 2039 | 2039 | 2039 | 2039 | 2039 | 2040 | 2040 | 2040 | 2040 | 2040 | 2040 | 2040 | 2040 | 2040 | 2040 | 2040 | 2040 | 2041 | 2041 | 2041 | 2041 | 2041 | 2041 | 2041 | 2041 | 2041 | 2041 | 2041 | 2041 | 2042 | 2042 | 2042 | 2042 | 2042 | 2042 | 2042 | 2042 | 2042 | 2042 | 2042 | 2042 | 2043 | 2043 | 2043 | 2043 | 2043 | 2043 | 2043 | 2043 | 2043 | 2043 | 2043 | 2043 | 2044 | 2044 | 2044 | 2044 | 2044 | 2044 | 2044 | 2044 | 2044 | 2044 | 2044 | 2044 | 2045 | 2045 | 2045 | 2045 | 2045 | 2045 | 2045 | 2045 | 2045 | 2045 | 2045 | 2045 | 2046 | 2046 | 2046 | 2046 | 2046 | 2046 | 2046 | 2046 | 2046 | 2046 | 2046 | 2046 | 2047 | 2047 | 2047 | 2047 | 2047 | 2047 | 2047 | 2047 | 2047 | 2047 | 2047 | 2047 | 2048 | 2048 | 2048 | 2048 | 2048 | 2048 | 2048 | 2048 | 2048 | 2048 | 2048 | 2048 | 2049 | 2049 | 2049 | 2049 | 2049 | 2049 | 2049 | 2049 | 2049 | 2049 | 2049 | 2049 | 2050 | 2050 | 2050 | 2050 | 2050 | 2050 | 2050 | 2050 | 2050 | 2050 | 2050 | 2050 | 2051 | 2051 | 2051 | 2051 | 2051 | 2051 | 2051 | 2051 | 2051 | 2051 | 2051 | 2051 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2052 | 2053 | 2053 | 2053 | 2053 | 2053 | 2053 | 2053 | 2053 | 2053 | 2053 | 2053 | 2053 | 2054 | 2054 | 2054 | 2054 | 2054 | 2054 | 2054 | 2054 | 2054 | 2054 | 2054 | 2054 | 2055 | 2055 | 2055 | 2055 | 2055 | 2055 | 2055 | 2055 | 2055 | 2055 | 2055 | 2055 | 2056 | 2056 | 2056 | 2056 | 2056 | 2056 | 2056 | 2056 | 2056 | 2056 | 2056 | 2056 | 2057 | 2057 | 2057 | 2057 | 2057 | 2057 | 2057 | 2057
Project Year |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32
Month |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | Peak
Frequency Flag |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
T&D Flag |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nominal Site Capacity - kW (0) |  | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.385 | 11.385 | 11.385 | 11.385 | 11.385 | 11.385 | 11.385 | 11.385 | 11.385 | 11.385 | 11.385 | 11.385 | 11.27 | 11.27 | 11.27 | 11.27 | 11.27 | 11.27 | 11.27 | 11.27 | 11.27 | 11.27 | 11.27 | 11.27 | 11.155 | 11.155 | 11.155 | 11.155 | 11.155 | 11.155 | 11.155 | 11.155 | 11.155 | 11.155 | 11.155 | 11.155 | 10.81 | 10.81 | 10.81 | 10.81 | 10.81 | 10.81 | 10.81 | 10.81 | 10.81 | 10.81 | 10.81 | 10.81 | 10.465 | 10.465 | 10.465 | 10.465 | 10.465 | 10.465 | 10.465 | 10.465 | 10.465 | 10.465 | 10.465 | 10.465 | 9.89 | 9.89 | 9.89 | 9.89 | 9.89 | 9.89 | 9.89 | 9.89 | 9.89 | 9.89 | 9.89 | 9.89 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 8.625 | 6.325 | 6.325 | 6.325 | 6.325 | 6.325 | 6.325 | 6.325 | 6.325 | 6.325 | 6.325 | 6.325 | 6.325 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 3.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Volume (1) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RNS Volume (1) |  | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.4 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.3 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Reserve Margin |  | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35%
Marginal Losses |  | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75% | 6.75%
[382 empty] | Month | Year | Beginning | Ending | Volume
Adjusted Capacity Volume (2) |  | 10.466 | 10.466 | 10.466 | 10.466 | 10.466 | 10.466 | 10.466 | 10.466 | 10.466 | 10.466 | 10.466 | 10.466 | 9.917 | 9.917 | 9.917 | 9.917 | 9.917 | 9.917 | 9.917 | 9.917 | 9.917 | 9.917 | 9.917 | 9.917 | 9.396 | 9.396 | 9.396 | 9.396 | 9.396 | 9.307 | 9.307 | 9.307 | 9.307 | 9.307 | 9.307 | 9.307 | 8.818 | 8.818 | 8.818 | 8.818 | 8.818 | 8.818 | 8.818 | 8.818 | 8.818 | 8.818 | 8.818 | 8.818 | 8.355 | 8.355 | 8.355 | 8.355 | 8.355 | 8.355 | 8.355 | 8.355 | 8.355 | 8.355 | 8.355 | 8.355 | 7.916 | 7.916 | 7.916 | 7.916 | 7.916 | 7.916 | 7.916 | 7.916 | 7.916 | 7.916 | 7.916 | 7.916 | 7.501 | 7.501 | 7.501 | 7.501 | 7.501 | 7.429 | 7.429 | 7.429 | 7.429 | 7.429 | 7.429 | 7.429 | 7.039 | 7.039 | 7.039 | 7.039 | 7.039 | 7.039 | 7.039 | 7.039 | 7.039 | 7.039 | 7.039 | 7.039 | 6.669 | 6.669 | 6.669 | 6.669 | 6.669 | 6.604 | 6.604 | 6.604 | 6.604 | 6.604 | 6.604 | 6.604 | 6.258 | 6.258 | 6.258 | 6.258 | 6.258 | 6.258 | 6.258 | 6.258 | 6.258 | 6.258 | 6.258 | 6.258 | 5.929 | 5.929 | 5.929 | 5.929 | 5.929 | 5.813 | 5.813 | 5.813 | 5.813 | 5.813 | 5.813 | 5.813 | 5.508 | 5.508 | 5.508 | 5.508 | 5.508 | 5.398 | 5.398 | 5.398 | 5.398 | 5.398 | 5.398 | 5.398 | 5.114 | 5.114 | 5.114 | 5.114 | 5.114 | 5.062 | 5.062 | 5.062 | 5.062 | 5.062 | 5.062 | 5.062 | 4.796 | 4.796 | 4.796 | 4.796 | 4.796 | 4.599 | 4.599 | 4.599 | 4.599 | 4.599 | 4.599 | 4.599 | 4.357 | 4.357 | 4.357 | 4.357 | 4.357 | 4.217 | 4.217 | 4.217 | 4.217 | 4.217 | 4.217 | 4.217 | 3.995 | 3.995 | 3.995 | 3.995 | 3.995 | 3.773 | 3.773 | 3.773 | 3.773 | 3.773 | 3.773 | 3.773 | 3.575 | 3.575 | 3.575 | 3.575 | 3.575 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 3.07 | 2.909 | 2.909 | 2.909 | 2.909 | 2.909 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.152 | 2.039 | 2.039 | 2.039 | 2.039 | 2.039 | 1.095 | 1.095 | 1.095 | 1.095 | 1.095 | 1.095 | 1.095 | 1.038 | 1.038 | 1.038 | 1.038 | 1.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 2025 | 2025-06-01 | 2026-05-31 | 10.5
Adjusted RNS Volume (2) |  | 0 | 6.444 | 6.444 | 6.444 | 6.444 | 6.444 | 6.444 | 6.444 | 6.444 | 6.444 | 6.444 | 6.444 | 6.074 | 6.074 | 6.074 | 6.074 | 6.074 | 6.074 | 6.074 | 6.074 | 6.074 | 6.074 | 6.074 | 6.074 | 5.724 | 5.67 | 5.67 | 5.67 | 5.67 | 5.67 | 5.67 | 5.67 | 5.67 | 5.67 | 5.67 | 5.67 | 5.344 | 5.344 | 5.344 | 5.344 | 5.344 | 5.344 | 5.344 | 5.344 | 5.344 | 5.344 | 5.344 | 5.344 | 5.037 | 5.037 | 5.037 | 5.037 | 5.037 | 5.037 | 5.037 | 5.037 | 5.037 | 5.037 | 5.037 | 5.037 | 4.747 | 4.747 | 4.747 | 4.747 | 4.747 | 4.747 | 4.747 | 4.747 | 4.747 | 4.747 | 4.747 | 4.747 | 4.474 | 4.431 | 4.431 | 4.431 | 4.431 | 4.431 | 4.431 | 4.431 | 4.431 | 4.431 | 4.431 | 4.431 | 4.176 | 4.176 | 4.176 | 4.176 | 4.176 | 4.176 | 4.176 | 4.176 | 4.176 | 4.176 | 4.176 | 4.176 | 3.936 | 3.898 | 3.898 | 3.898 | 3.898 | 3.898 | 3.898 | 3.898 | 3.898 | 3.898 | 3.898 | 3.898 | 3.674 | 3.674 | 3.674 | 3.674 | 3.674 | 3.674 | 3.674 | 3.674 | 3.674 | 3.674 | 3.674 | 3.674 | 3.463 | 3.395 | 3.395 | 3.395 | 3.395 | 3.395 | 3.395 | 3.395 | 3.395 | 3.395 | 3.395 | 3.395 | 3.199 | 3.135 | 3.135 | 3.135 | 3.135 | 3.135 | 3.135 | 3.135 | 3.135 | 3.135 | 3.135 | 3.135 | 2.955 | 2.925 | 2.925 | 2.925 | 2.925 | 2.925 | 2.925 | 2.925 | 2.925 | 2.925 | 2.925 | 2.925 | 2.757 | 2.643 | 2.643 | 2.643 | 2.643 | 2.643 | 2.643 | 2.643 | 2.643 | 2.643 | 2.643 | 2.643 | 2.491 | 2.411 | 2.411 | 2.411 | 2.411 | 2.411 | 2.411 | 2.411 | 2.411 | 2.411 | 2.411 | 2.411 | 2.272 | 2.146 | 2.146 | 2.146 | 2.146 | 2.146 | 2.146 | 2.146 | 2.146 | 2.146 | 2.146 | 2.146 | 2.023 | 1.737 | 1.737 | 1.737 | 1.737 | 1.737 | 1.737 | 1.737 | 1.737 | 1.737 | 1.737 | 1.737 | 1.637 | 1.211 | 1.211 | 1.211 | 1.211 | 1.211 | 1.211 | 1.211 | 1.211 | 1.211 | 1.211 | 1.211 | 1.141 | 0.613 | 0.613 | 0.613 | 0.613 | 0.613 | 0.613 | 0.613 | 0.613 | 0.613 | 0.613 | 0.613 | 0.578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 2026 | 2026-06-01 | 2027-05-31 | 10.5
[382 empty] | 8 | 2027 | 2027-06-01 | 2028-05-31 | 10.5
RNS Price - $/kW-month |  | 17.4941 | 17.5378 | 17.5378 | 17.5378 | 17.5378 | 17.5378 | 17.5378 | 17.5378 | 17.5378 | 17.5378 | 17.5378 | 17.5378 | 18.3578 | 18.4023 | 18.4023 | 18.4023 | 18.4023 | 18.4023 | 18.4023 | 18.4023 | 18.4023 | 18.4023 | 18.4023 | 18.4023 | 19.3023 | 19.3478 | 19.3478 | 19.3478 | 19.3478 | 19.3478 | 19.3478 | 19.3478 | 19.3478 | 19.3478 | 19.3478 | 19.3478 | 20.1678 | 20.2141 | 20.2141 | 20.2141 | 20.2141 | 20.2141 | 20.2141 | 20.2141 | 20.2141 | 20.2141 | 20.2141 | 20.2141 | 20.6641 | 20.7114 | 20.7114 | 20.7114 | 20.7114 | 20.7114 | 20.7114 | 20.7114 | 20.7114 | 20.7114 | 20.7114 | 20.7114 | 20.9814 | 21.0296 | 21.0296 | 21.0296 | 21.0296 | 21.0296 | 21.0296 | 21.0296 | 21.0296 | 21.0296 | 21.0296 | 21.0296 | 21.3096 | 21.3588 | 21.3588 | 21.3588 | 21.3588 | 21.3588 | 21.3588 | 21.3588 | 21.3588 | 21.3588 | 21.3588 | 21.3588 | 21.6488 | 21.699 | 21.699 | 21.699 | 21.699 | 21.699 | 21.699 | 21.699 | 21.699 | 21.699 | 21.699 | 21.699 | 21.979 | 22.0302 | 22.0302 | 22.0302 | 22.0302 | 22.0302 | 22.0302 | 22.0302 | 22.0302 | 22.0302 | 22.0302 | 22.0302 | 22.3202 | 22.3724 | 22.3724 | 22.3724 | 22.3724 | 22.3724 | 22.3724 | 22.3724 | 22.3724 | 22.3724 | 22.3724 | 22.3724 | 22.6724 | 22.7256 | 22.7256 | 22.7256 | 22.7256 | 22.7256 | 22.7256 | 22.7256 | 22.7256 | 22.7256 | 22.7256 | 22.7256 | 23.0256 | 23.0799 | 23.0799 | 23.0799 | 23.0799 | 23.0799 | 23.0799 | 23.0799 | 23.0799 | 23.0799 | 23.0799 | 23.0799 | 23.3799 | 23.4353 | 23.4353 | 23.4353 | 23.4353 | 23.4353 | 23.4353 | 23.4353 | 23.4353 | 23.4353 | 23.4353 | 23.4353 | 23.7453 | 23.8018 | 23.8018 | 23.8018 | 23.8018 | 23.8018 | 23.8018 | 23.8018 | 23.8018 | 23.8018 | 23.8018 | 23.8018 | 24.1218 | 24.1795 | 24.1795 | 24.1795 | 24.1795 | 24.1795 | 24.1795 | 24.1795 | 24.1795 | 24.1795 | 24.1795 | 24.1795 | 24.4895 | 24.5483 | 24.5483 | 24.5483 | 24.5483 | 24.5483 | 24.5483 | 24.5483 | 24.5483 | 24.5483 | 24.5483 | 24.5483 | 24.8783 | 24.9382 | 24.9382 | 24.9382 | 24.9382 | 24.9382 | 24.9382 | 24.9382 | 24.9382 | 24.9382 | 24.9382 | 24.9382 | 25.2682 | 25.3294 | 25.3294 | 25.3294 | 25.3294 | 25.3294 | 25.3294 | 25.3294 | 25.3294 | 25.3294 | 25.3294 | 25.3294 | 25.6594 | 25.7218 | 25.7218 | 25.7218 | 25.7218 | 25.7218 | 25.7218 | 25.7218 | 25.7218 | 25.7218 | 25.7218 | 25.7218 | 26.0618 | 26.1254 | 26.1254 | 26.1254 | 26.1254 | 26.1254 | 26.1254 | 26.1254 | 26.1254 | 26.1254 | 26.1254 | 26.1254 | 26.4654 | 26.5303 | 26.5303 | 26.5303 | 26.5303 | 26.5303 | 26.5303 | 26.5303 | 26.5303 | 26.5303 | 26.5303 | 26.5303 | 26.8803 | 26.9465 | 26.9465 | 26.9465 | 26.9465 | 26.9465 | 26.9465 | 26.9465 | 26.9465 | 26.9465 | 26.9465 | 26.9465 | 27.2965 | 27.3641 | 27.3641 | 27.3641 | 27.3641 | 27.3641 | 27.3641 | 27.3641 | 27.3641 | 27.3641 | 27.3641 | 27.3641 | 27.7241 | 27.7929 | 27.7929 | 27.7929 | 27.7929 | 27.7929 | 27.7929 | 27.7929 | 27.7929 | 27.7929 | 27.7929 | 27.7929 | 28.1629 | 28.2332 | 28.2332 | 28.2332 | 28.2332 | 28.2332 | 28.2332 | 28.2332 | 28.2332 | 28.2332 | 28.2332 | 28.2332 | 28.5932 | 28.6649 | 28.6649 | 28.6649 | 28.6649 | 28.6649 | 28.6649 | 28.6649 | 28.6649 | 28.6649 | 28.6649 | 28.6649 | 29.0449 | 29.118 | 29.118 | 29.118 | 29.118 | 29.118 | 29.118 | 29.118 | 29.118 | 29.118 | 29.118 | 29.118 | 29.498 | 29.5725 | 29.5725 | 29.5725 | 29.5725 | 29.5725 | 29.5725 | 29.5725 | 29.5725 | 29.5725 | 29.5725 | 29.5725 | 29.9625 | 30.0386 | 30.0386 | 30.0386 | 30.0386 | 30.0386 | 30.0386 | 30.0386 | 30.0386 | 30.0386 | 30.0386 | 30.0386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 2028 | 2028-06-01 | 2029-05-31 | 10.4
Capacity Price - $/kW-month |  | 2.53 | 2.53 | 2.53 | 2.53 | 2.53 | 2.59 | 2.59 | 2.59 | 2.59 | 2.59 | 2.59 | 2.59 | 2.59 | 2.59 | 2.59 | 2.59 | 2.59 | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | 3.58 | 5.349 | 5.349 | 5.349 | 5.349 | 5.349 | 5.349 | 5.349 | 5.349 | 5.349 | 5.349 | 5.349 | 5.349 | 6.1398 | 6.1398 | 6.1398 | 6.1398 | 6.1398 | 6.1398 | 6.1398 | 6.1398 | 6.1398 | 6.1398 | 6.1398 | 6.1398 | 6.3795 | 6.3795 | 6.3795 | 6.3795 | 6.3795 | 6.3795 | 6.3795 | 6.3795 | 6.3795 | 6.3795 | 6.3795 | 6.3795 | 6.6687 | 6.6687 | 6.6687 | 6.6687 | 6.6687 | 6.6687 | 6.6687 | 6.6687 | 6.6687 | 6.6687 | 6.6687 | 6.6687 | 7.289 | 7.289 | 7.289 | 7.289 | 7.289 | 7.289 | 7.289 | 7.289 | 7.289 | 7.289 | 7.289 | 7.289 | 7.5317 | 7.5317 | 7.5317 | 7.5317 | 7.5317 | 7.5317 | 7.5317 | 7.5317 | 7.5317 | 7.5317 | 7.5317 | 7.5317 | 7.9506 | 7.9506 | 7.9506 | 7.9506 | 7.9506 | 7.9506 | 7.9506 | 7.9506 | 7.9506 | 7.9506 | 7.9506 | 7.9506 | 8.7393 | 8.7393 | 8.7393 | 8.7393 | 8.7393 | 8.7393 | 8.7393 | 8.7393 | 8.7393 | 8.7393 | 8.7393 | 8.7393 | 12.4472 | 12.4472 | 12.4472 | 12.4472 | 12.4472 | 12.4472 | 12.4472 | 12.4472 | 12.4472 | 12.4472 | 12.4472 | 12.4472 | 13.3672 | 13.3672 | 13.3672 | 13.3672 | 13.3672 | 13.3672 | 13.3672 | 13.3672 | 13.3672 | 13.3672 | 13.3672 | 13.3672 | 14.1264 | 14.1264 | 14.1264 | 14.1264 | 14.1264 | 14.1264 | 14.1264 | 14.1264 | 14.1264 | 14.1264 | 14.1264 | 14.1264 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 14.951 | 15.3248 | 15.3248 | 15.3248 | 15.3248 | 15.3248 | 15.3248 | 15.3248 | 15.3248 | 15.3248 | 15.3248 | 15.3248 | 15.3248 | 15.7079 | 15.7079 | 15.7079 | 15.7079 | 15.7079 | 15.7079 | 15.7079 | 15.7079 | 15.7079 | 15.7079 | 15.7079 | 15.7079 | 16.1006 | 16.1006 | 16.1006 | 16.1006 | 16.1006 | 16.1006 | 16.1006 | 16.1006 | 16.1006 | 16.1006 | 16.1006 | 16.1006 | 16.5031 | 16.5031 | 16.5031 | 16.5031 | 16.5031 | 16.5031 | 16.5031 | 16.5031 | 16.5031 | 16.5031 | 16.5031 | 16.5031 | 16.9157 | 16.9157 | 16.9157 | 16.9157 | 16.9157 | 16.9157 | 16.9157 | 16.9157 | 16.9157 | 16.9157 | 16.9157 | 16.9157 | 17.3047 | 17.3047 | 17.3047 | 17.3047 | 17.3047 | 17.3047 | 17.3047 | 17.3047 | 17.3047 | 17.3047 | 17.3047 | 17.3047 | 17.7027 | 17.7027 | 17.7027 | 17.7027 | 17.7027 | 17.7027 | 17.7027 | 17.7027 | 17.7027 | 17.7027 | 17.7027 | 17.7027 | 18.1099 | 18.1099 | 18.1099 | 18.1099 | 18.1099 | 18.1099 | 18.1099 | 18.1099 | 18.1099 | 18.1099 | 18.1099 | 18.1099 | 18.5264 | 18.5264 | 18.5264 | 18.5264 | 18.5264 | 18.5264 | 18.5264 | 18.5264 | 18.5264 | 18.5264 | 18.5264 | 18.5264 | 18.9525 | 18.9525 | 18.9525 | 18.9525 | 18.9525 | 18.9525 | 18.9525 | 18.9525 | 18.9525 | 18.9525 | 18.9525 | 18.9525 | 19.3885 | 19.3885 | 19.3885 | 19.3885 | 19.3885 | 19.3885 | 19.3885 | 19.3885 | 19.3885 | 19.3885 | 19.3885 | 19.3885 | 19.8344 | 19.8344 | 19.8344 | 19.8344 | 19.8344 | 19.8344 | 19.8344 | 19.8344 | 19.8344 | 19.8344 | 19.8344 | 19.8344 | 20.2906 | 20.2906 | 20.2906 | 20.2906 | 20.2906 | 20.2906 | 20.2906 | 20.2906 | 20.2906 | 20.2906 | 20.2906 | 20.2906 | 20.7573 | 20.7573 | 20.7573 | 20.7573 | 20.7573 | 20.7573 | 20.7573 | 20.7573 | 20.7573 | 20.7573 | 20.7573 | 20.7573 | 21.2347 | 21.2347 | 21.2347 | 21.2347 | 21.2347 | 21.2347 | 21.2347 | 21.2347 | 21.2347 | 21.2347 | 21.2347 | 21.2347 | 21.7231 | 21.7231 | 21.7231 | 21.7231 | 21.7231 | 21.7231 | 21.7231 | 21.7231 | 21.7231 | 21.7231 | 21.7231 | 21.7231 | 22.2227 | 22.2227 | 22.2227 | 22.2227 | 22.2227 | 22.2227 | 22.2227 | 22.2227 | 22.2227 | 22.2227 | 22.2227 | 22.2227 | 0 | 0 | 0 | 8 | 2029 | 2029-06-01 | 2030-05-31 | 10.4
[382 empty] | 8 | 2030 | 2030-06-01 | 2031-05-31 | 10.4
Revenues | [381 empty] | 8 | 2031 | 2031-06-01 | 2032-05-31 | 10.4
Energy |  | 9.0876 | 9.1607 | 10.4208 | 11.4272 | 11.4897 | 12.4685 | 13.8749 | 14.1731 | 12.2969 | 11.6303 | 10.5986 | 10.472 | 8.9837 | 9.6756 | 10.8035 | 12.0124 | 12.4687 | 12.8287 | 14.3701 | 14.7245 | 12.5446 | 12.6318 | 11.5523 | 10.8069 | 12.4373 | 12.6922 | 10.9204 | 11.3082 | 11.4415 | 11.6253 | 12.3294 | 11.4305 | 11.3766 | 11.2746 | 10.9637 | 10.7687 | 12.5102 | 12.524 | 11.2129 | 11.5934 | 11.6181 | 11.765 | 12.4808 | 11.7141 | 11.558 | 11.6073 | 11.2998 | 10.8561 | 12.8483 | 12.8896 | 11.4268 | 11.739 | 11.9198 | 12.0893 | 12.6258 | 11.9177 | 11.7233 | 11.9381 | 11.3002 | 11.907 | 13.4586 | 12.8338 | 11.6951 | 11.9891 | 12.0827 | 12.3265 | 12.7784 | 12.3096 | 12.1145 | 12.2386 | 11.5979 | 12.0716 | 13.7911 | 13.9321 | 11.8465 | 12.2254 | 12.2419 | 12.2671 | 12.8382 | 12.5936 | 12.1335 | 12.4924 | 11.5506 | 13.4967 | 14.2659 | 13.9421 | 12.104 | 12.4262 | 12.3483 | 12.4569 | 12.9772 | 12.9767 | 12.2715 | 12.8288 | 12.0189 | 12.7943 | 14.4088 | 14.0819 | 12.2264 | 12.5516 | 12.473 | 12.5826 | 13.1078 | 13.1074 | 12.3955 | 12.9581 | 12.1405 | 12.9232 | 14.697 | 14.3636 | 12.4709 | 12.8027 | 12.7225 | 12.8343 | 13.37 | 13.3695 | 12.6434 | 13.2173 | 12.3833 | 13.1817 | 14.7153 | 14.3787 | 12.4683 | 12.8032 | 12.7223 | 12.8351 | 13.3758 | 13.3754 | 12.6425 | 13.2217 | 12.3799 | 13.1858 | 14.7496 | 14.4063 | 12.4577 | 12.7993 | 12.7167 | 12.8318 | 13.3834 | 13.3829 | 12.6353 | 13.2261 | 12.3675 | 13.1895 | 14.912 | 14.5619 | 12.5743 | 12.9227 | 12.8384 | 12.9559 | 13.5184 | 13.518 | 12.7554 | 13.3581 | 12.4822 | 13.3207 | 14.6473 | 14.2939 | 12.2878 | 12.6395 | 12.5545 | 12.673 | 13.2408 | 13.2403 | 12.4707 | 13.0789 | 12.195 | 13.0412 | 14.5039 | 14.1473 | 12.1229 | 12.4778 | 12.392 | 12.5116 | 13.0845 | 13.084 | 12.3074 | 12.9212 | 12.0292 | 12.8831 | 14.0904 | 13.7267 | 11.6618 | 12.0238 | 11.9363 | 12.0582 | 12.6427 | 12.6422 | 11.85 | 12.4761 | 11.5662 | 12.4372 | 12.6266 | 12.2595 | 10.176 | 10.5412 | 10.4529 | 10.576 | 11.1657 | 11.1652 | 10.3659 | 10.9976 | 10.0796 | 10.9585 | 10.0976 | 9.7232 | 7.598 | 7.9706 | 7.8805 | 8.006 | 8.6075 | 8.607 | 7.7917 | 8.4361 | 7.4996 | 8.3961 | 6.5422 | 6.1644 | 4.0203 | 4.3962 | 4.3053 | 4.432 | 5.0388 | 5.0383 | 4.2157 | 4.8658 | 3.9211 | 4.8255 | 2.256 | 1.8707 | -0.31627 | 0.06712 | -0.025569 | 0.10363 | 0.72263 | 0.72211 | -0.11692 | 0.54618 | -0.41751 | 0.50506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [20 empty] | 8 | 2032 | 2032-06-01 | 2033-05-31 | 10.3
DASI |  | 0.5355 | 0.5355 | 0.5355 | 0.5355 | 0.5355 | 0.5355 | 0.5355 | 0.5355 | 0.5355 | 0.5355 | 0.5355 | 0.5355 | 0.54621 | 0.54621 | 0.54621 | 0.54621 | 0.54621 | 0.54621 | 0.54621 | 0.54621 | 0.54621 | 0.54621 | 0.54621 | 0.54621 | 0.55183 | 0.55183 | 0.55183 | 0.55183 | 0.55183 | 0.55183 | 0.55183 | 0.55183 | 0.55183 | 0.55183 | 0.55183 | 0.55183 | 0.56286 | 0.56286 | 0.56286 | 0.56286 | 0.56286 | 0.56286 | 0.56286 | 0.56286 | 0.56286 | 0.56286 | 0.56286 | 0.56286 | 0.57412 | 0.57412 | 0.57412 | 0.57412 | 0.57412 | 0.57412 | 0.57412 | 0.57412 | 0.57412 | 0.57412 | 0.57412 | 0.57412 | 0.5856 | 0.5856 | 0.5856 | 0.5856 | 0.5856 | 0.5856 | 0.5856 | 0.5856 | 0.5856 | 0.5856 | 0.5856 | 0.5856 | 0.59157 | 0.59157 | 0.59157 | 0.59157 | 0.59157 | 0.59157 | 0.59157 | 0.59157 | 0.59157 | 0.59157 | 0.59157 | 0.59157 | 0.6034 | 0.6034 | 0.6034 | 0.6034 | 0.6034 | 0.6034 | 0.6034 | 0.6034 | 0.6034 | 0.6034 | 0.6034 | 0.6034 | 0.6095 | 0.6095 | 0.6095 | 0.6095 | 0.6095 | 0.6095 | 0.6095 | 0.6095 | 0.6095 | 0.6095 | 0.6095 | 0.6095 | 0.62169 | 0.62169 | 0.62169 | 0.62169 | 0.62169 | 0.62169 | 0.62169 | 0.62169 | 0.62169 | 0.62169 | 0.62169 | 0.62169 | 0.62169 | 0.62169 | 0.62169 | 0.62169 | 0.62169 | 0.62169 | 0.62169 | 0.62169 | 0.62169 | 0.62169 | 0.62169 | 0.62169 | 0.62144 | 0.62144 | 0.62144 | 0.62144 | 0.62144 | 0.62144 | 0.62144 | 0.62144 | 0.62144 | 0.62144 | 0.62144 | 0.62144 | 0.6274 | 0.6274 | 0.6274 | 0.6274 | 0.6274 | 0.6274 | 0.6274 | 0.6274 | 0.6274 | 0.6274 | 0.6274 | 0.6274 | 0.61356 | 0.61356 | 0.61356 | 0.61356 | 0.61356 | 0.61356 | 0.61356 | 0.61356 | 0.61356 | 0.61356 | 0.61356 | 0.61356 | 0.60564 | 0.60564 | 0.60564 | 0.60564 | 0.60564 | 0.60564 | 0.60564 | 0.60564 | 0.60564 | 0.60564 | 0.60564 | 0.60564 | 0.58343 | 0.58343 | 0.58343 | 0.58343 | 0.58343 | 0.58343 | 0.58343 | 0.58343 | 0.58343 | 0.58343 | 0.58343 | 0.58343 | 0.51109 | 0.51109 | 0.51109 | 0.51109 | 0.51109 | 0.51109 | 0.51109 | 0.51109 | 0.51109 | 0.51109 | 0.51109 | 0.51109 | 0.38563 | 0.38563 | 0.38563 | 0.38563 | 0.38563 | 0.38563 | 0.38563 | 0.38563 | 0.38563 | 0.38563 | 0.38563 | 0.38563 | 0.21124 | 0.21124 | 0.21124 | 0.21124 | 0.21124 | 0.21124 | 0.21124 | 0.21124 | 0.21124 | 0.21124 | 0.21124 | 0.21124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rate 1 |  | 5.6207 | 5.6207 | 5.6207 | 5.6207 | 5.6207 | 5.6207 | 5.6207 | 5.6207 | 5.6207 | 5.6207 | 5.6207 | 5.6207 | 5.7332 | 5.7332 | 5.7332 | 5.7332 | 5.7332 | 5.7332 | 5.7332 | 5.7332 | 5.7332 | 5.7332 | 5.7332 | 5.7332 | 5.7336 | 5.7336 | 5.7336 | 5.7336 | 5.7336 | 5.7336 | 5.7336 | 5.7336 | 5.7336 | 5.7336 | 5.7336 | 5.7336 | 5.8483 | 5.8483 | 5.8483 | 5.8483 | 5.8483 | 5.8483 | 5.8483 | 5.8483 | 5.8483 | 5.8483 | 5.8483 | 5.8483 | 5.9653 | 5.9653 | 5.9653 | 5.9653 | 5.9653 | 5.9653 | 5.9653 | 5.9653 | 5.9653 | 5.9653 | 5.9653 | 5.9653 | 6.0846 | 6.0846 | 6.0846 | 6.0846 | 6.0846 | 6.0846 | 6.0846 | 6.0846 | 6.0846 | 6.0846 | 6.0846 | 6.0846 | 6.0839 | 6.0839 | 6.0839 | 6.0839 | 6.0839 | 6.0839 | 6.0839 | 6.0839 | 6.0839 | 6.0839 | 6.0839 | 6.0839 | 6.2055 | 6.2055 | 6.2055 | 6.2055 | 6.2055 | 6.2055 | 6.2055 | 6.2055 | 6.2055 | 6.2055 | 6.2055 | 6.2055 | 6.2036 | 6.2036 | 6.2036 | 6.2036 | 6.2036 | 6.2036 | 6.2036 | 6.2036 | 6.2036 | 6.2036 | 6.2036 | 6.2036 | 6.3277 | 6.3277 | 6.3277 | 6.3277 | 6.3277 | 6.3277 | 6.3277 | 6.3277 | 6.3277 | 6.3277 | 6.3277 | 6.3277 | 6.2617 | 6.2617 | 6.2617 | 6.2617 | 6.2617 | 6.2617 | 6.2617 | 6.2617 | 6.2617 | 6.2617 | 6.2617 | 6.2617 | 6.2592 | 6.2592 | 6.2592 | 6.2592 | 6.2592 | 6.2592 | 6.2592 | 6.2592 | 6.2592 | 6.2592 | 6.2592 | 6.2592 | 6.3193 | 6.3193 | 6.3193 | 6.3193 | 6.3193 | 6.3193 | 6.3193 | 6.3193 | 6.3193 | 6.3193 | 6.3193 | 6.3193 | 6.1148 | 6.1148 | 6.1148 | 6.1148 | 6.1148 | 6.1148 | 6.1148 | 6.1148 | 6.1148 | 6.1148 | 6.1148 | 6.1148 | 5.9717 | 5.9717 | 5.9717 | 5.9717 | 5.9717 | 5.9717 | 5.9717 | 5.9717 | 5.9717 | 5.9717 | 5.9717 | 5.9717 | 5.7527 | 5.7527 | 5.7527 | 5.7527 | 5.7527 | 5.7527 | 5.7527 | 5.7527 | 5.7527 | 5.7527 | 5.7527 | 5.7527 | 4.9852 | 4.9852 | 4.9852 | 4.9852 | 4.9852 | 4.9852 | 4.9852 | 4.9852 | 4.9852 | 4.9852 | 4.9852 | 4.9852 | 3.7614 | 3.7614 | 3.7614 | 3.7614 | 3.7614 | 3.7614 | 3.7614 | 3.7614 | 3.7614 | 3.7614 | 3.7614 | 3.7614 | 2.038 | 2.038 | 2.038 | 2.038 | 2.038 | 2.038 | 2.038 | 2.038 | 2.038 | 2.038 | 2.038 | 2.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Frequency |  | 15.9216 | 15.9216 | 15.9216 | 15.9216 | 15.9216 | 15.9216 | 15.9216 | 15.9216 | 15.9216 | 15.9216 | 15.9216 | 15.9216 | 13.5334 | 13.5334 | 13.5334 | 13.5334 | 13.5334 | 13.5334 | 13.5334 | 13.5334 | 13.5334 | 13.5334 | 13.5334 | 13.5334 | 11.3938 | 11.3938 | 11.3938 | 11.3938 | 11.3938 | 11.3938 | 11.3938 | 11.3938 | 11.3938 | 11.3938 | 11.3938 | 11.3938 | 9.6848 | 9.6848 | 9.6848 | 9.6848 | 9.6848 | 9.6848 | 9.6848 | 9.6848 | 9.6848 | 9.6848 | 9.6848 | 9.6848 | 8.232 | 8.232 | 8.232 | 8.232 | 8.232 | 8.232 | 8.232 | 8.232 | 8.232 | 8.232 | 8.232 | 8.232 | 6.9972 | 6.9972 | 6.9972 | 6.9972 | 6.9972 | 6.9972 | 6.9972 | 6.9972 | 6.9972 | 6.9972 | 6.9972 | 6.9972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
T&D Deferral |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62.2292 | 62.2292 | 62.2292 | 62.2292 | 62.2292 | 62.2292 | 62.2292 | 62.2292 | 62.2292 | 62.2292 | 62.2292 | 62.2292 | 62.2292 | 62.2292 | 62.2292 | 62.2292 | 62.2292 | 62.2292 | 62.2292 | 62.2292 | 62.2292 | 62.2292 | 62.2292 | 62.2292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Power Factor/VAR support |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity |  | 26.48 | 26.48 | 26.48 | 26.48 | 26.48 | 27.11 | 27.11 | 27.11 | 27.11 | 27.11 | 27.11 | 27.11 | 25.69 | 25.69 | 25.69 | 25.69 | 25.69 | 35.5 | 35.5 | 35.5 | 35.5 | 35.5 | 35.5 | 35.5 | 33.64 | 33.64 | 33.64 | 33.64 | 33.64 | 49.78 | 49.78 | 49.78 | 49.78 | 49.78 | 49.78 | 49.78 | 47.17 | 47.17 | 47.17 | 47.17 | 47.17 | 54.14 | 54.14 | 54.14 | 54.14 | 54.14 | 54.14 | 54.14 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 52.79 | 52.79 | 52.79 | 52.79 | 52.79 | 52.79 | 52.79 | 50.02 | 50.02 | 50.02 | 50.02 | 50.02 | 54.15 | 54.15 | 54.15 | 54.15 | 54.15 | 54.15 | 54.15 | 51.31 | 51.31 | 51.31 | 51.31 | 51.31 | 53.02 | 53.02 | 53.02 | 53.02 | 53.02 | 53.02 | 53.02 | 50.23 | 50.23 | 50.23 | 50.23 | 50.23 | 52.51 | 52.51 | 52.51 | 52.51 | 52.51 | 52.51 | 52.51 | 49.75 | 49.75 | 49.75 | 49.75 | 49.75 | 54.69 | 54.69 | 54.69 | 54.69 | 54.69 | 54.69 | 54.69 | 51.82 | 51.82 | 51.82 | 51.82 | 51.82 | 72.36 | 72.36 | 72.36 | 72.36 | 72.36 | 72.36 | 72.36 | 68.56 | 68.56 | 68.56 | 68.56 | 68.56 | 72.16 | 72.16 | 72.16 | 72.16 | 72.16 | 72.16 | 72.16 | 68.36 | 68.36 | 68.36 | 68.36 | 68.36 | 71.51 | 71.51 | 71.51 | 71.51 | 71.51 | 71.51 | 71.51 | 67.75 | 67.75 | 67.75 | 67.75 | 67.75 | 68.76 | 68.76 | 68.76 | 68.76 | 68.76 | 68.76 | 68.76 | 65.14 | 65.14 | 65.14 | 65.14 | 65.14 | 64.62 | 64.62 | 64.62 | 64.62 | 64.62 | 64.62 | 64.62 | 61.22 | 61.22 | 61.22 | 61.22 | 61.22 | 59.27 | 59.27 | 59.27 | 59.27 | 59.27 | 59.27 | 59.27 | 56.16 | 56.16 | 56.16 | 56.16 | 56.16 | 49.43 | 49.43 | 49.43 | 49.43 | 49.43 | 49.43 | 49.43 | 46.84 | 46.84 | 46.84 | 46.84 | 46.84 | 35.51 | 35.51 | 35.51 | 35.51 | 35.51 | 35.51 | 35.51 | 33.65 | 33.65 | 33.65 | 33.65 | 33.65 | 18.52 | 18.52 | 18.52 | 18.52 | 18.52 | 18.52 | 18.52 | 17.56 | 17.56 | 17.56 | 17.56 | 17.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 2033 | 2033-06-01 | 2034-05-31 | 10.3
RNS |  | 0 | 113.01 | 113.01 | 113.01 | 113.01 | 113.01 | 113.01 | 113.01 | 113.01 | 113.01 | 113.01 | 113.01 | 111.5 | 111.78 | 111.78 | 111.78 | 111.78 | 111.78 | 111.78 | 111.78 | 111.78 | 111.78 | 111.78 | 111.78 | 110.49 | 109.7 | 109.7 | 109.7 | 109.7 | 109.7 | 109.7 | 109.7 | 109.7 | 109.7 | 109.7 | 109.7 | 107.78 | 108.02 | 108.02 | 108.02 | 108.02 | 108.02 | 108.02 | 108.02 | 108.02 | 108.02 | 108.02 | 108.02 | 104.09 | 104.32 | 104.32 | 104.32 | 104.32 | 104.32 | 104.32 | 104.32 | 104.32 | 104.32 | 104.32 | 104.32 | 99.6 | 99.83 | 99.83 | 99.83 | 99.83 | 99.83 | 99.83 | 99.83 | 99.83 | 99.83 | 99.83 | 99.83 | 95.34 | 94.64 | 94.64 | 94.64 | 94.64 | 94.64 | 94.64 | 94.64 | 94.64 | 94.64 | 94.64 | 94.64 | 90.41 | 90.61 | 90.61 | 90.61 | 90.61 | 90.61 | 90.61 | 90.61 | 90.61 | 90.61 | 90.61 | 90.61 | 86.51 | 85.87 | 85.87 | 85.87 | 85.87 | 85.87 | 85.87 | 85.87 | 85.87 | 85.87 | 85.87 | 85.87 | 82 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 78.51 | 77.15 | 77.15 | 77.15 | 77.15 | 77.15 | 77.15 | 77.15 | 77.15 | 77.15 | 77.15 | 77.15 | 73.66 | 72.36 | 72.36 | 72.36 | 72.36 | 72.36 | 72.36 | 72.36 | 72.36 | 72.36 | 72.36 | 72.36 | 69.09 | 68.55 | 68.55 | 68.55 | 68.55 | 68.55 | 68.55 | 68.55 | 68.55 | 68.55 | 68.55 | 68.55 | 65.47 | 62.91 | 62.91 | 62.91 | 62.91 | 62.91 | 62.91 | 62.91 | 62.91 | 62.91 | 62.91 | 62.91 | 60.09 | 58.3 | 58.3 | 58.3 | 58.3 | 58.3 | 58.3 | 58.3 | 58.3 | 58.3 | 58.3 | 58.3 | 55.64 | 52.68 | 52.68 | 52.68 | 52.68 | 52.68 | 52.68 | 52.68 | 52.68 | 52.68 | 52.68 | 52.68 | 50.33 | 43.32 | 43.32 | 43.32 | 43.32 | 43.32 | 43.32 | 43.32 | 43.32 | 43.32 | 43.32 | 43.32 | 41.36 | 30.67 | 30.67 | 30.67 | 30.67 | 30.67 | 30.67 | 30.67 | 30.67 | 30.67 | 30.67 | 30.67 | 29.28 | 15.77 | 15.77 | 15.77 | 15.77 | 15.77 | 15.77 | 15.77 | 15.77 | 15.77 | 15.77 | 15.77 | 15.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 2034 | 2034-06-01 | 2035-05-31 | 10.2
Total Revenues |  | 57.6455 | 170.7286 | 171.9887 | 172.9951 | 173.0576 | 174.6664 | 176.0728 | 176.3709 | 174.4948 | 173.8282 | 172.7965 | 172.6699 | 165.9864 | 166.9584 | 168.0863 | 169.2952 | 169.7514 | 179.9215 | 181.4629 | 181.8173 | 179.6374 | 179.7246 | 178.645 | 177.8997 | 174.2466 | 173.7114 | 171.9397 | 172.3274 | 172.4608 | 188.7846 | 189.4887 | 188.5897 | 188.5359 | 188.4339 | 188.123 | 187.928 | 183.5561 | 183.8099 | 182.4989 | 182.8793 | 182.9041 | 190.0209 | 190.7368 | 189.9701 | 189.8139 | 189.8632 | 189.5558 | 189.112 | 183.0098 | 183.2811 | 181.8183 | 182.1304 | 182.3112 | 184.4807 | 185.0173 | 184.3092 | 184.1147 | 184.3295 | 183.6917 | 184.2984 | 177.226 | 176.8312 | 175.6925 | 175.9865 | 176.0801 | 178.6139 | 179.0658 | 178.5971 | 178.4019 | 178.526 | 177.8853 | 178.359 | 228.0557 | 227.4967 | 225.4111 | 225.79 | 225.8065 | 229.9617 | 230.5328 | 230.2883 | 229.8281 | 230.187 | 229.2452 | 231.1913 | 225.0241 | 224.9002 | 223.0621 | 223.3843 | 223.3064 | 225.125 | 225.6453 | 225.6448 | 224.9396 | 225.497 | 224.687 | 225.4624 | 157.9619 | 156.995 | 155.1394 | 155.4647 | 155.3861 | 157.7757 | 158.3009 | 158.3004 | 157.5886 | 158.1512 | 157.3335 | 158.1163 | 153.3963 | 153.2629 | 151.3702 | 151.702 | 151.6218 | 156.6736 | 157.2093 | 157.2089 | 156.4827 | 157.0566 | 156.2226 | 157.021 | 151.9287 | 150.2322 | 148.3217 | 148.6566 | 148.5757 | 169.2285 | 169.7693 | 169.7688 | 169.0359 | 169.6151 | 168.7733 | 169.5792 | 163.8503 | 162.207 | 160.2584 | 160.6 | 160.5174 | 164.2325 | 164.784 | 164.7836 | 164.036 | 164.6268 | 163.7682 | 164.5902 | 159.3087 | 158.4185 | 156.4309 | 156.7794 | 156.6951 | 159.9625 | 160.5251 | 160.5246 | 159.7621 | 160.3647 | 159.4889 | 160.3274 | 154.5956 | 151.6822 | 149.6762 | 150.0279 | 149.9428 | 151.0713 | 151.6391 | 151.6386 | 150.8691 | 151.4773 | 150.5933 | 151.4396 | 146.3112 | 144.1646 | 142.1402 | 142.4951 | 142.4093 | 142.0089 | 142.5819 | 142.5814 | 141.8047 | 142.4185 | 141.5265 | 142.3805 | 137.2866 | 133.9628 | 131.898 | 132.2599 | 132.1724 | 130.3444 | 130.9288 | 130.9283 | 130.1362 | 130.7622 | 129.8524 | 130.7234 | 124.6129 | 117.2358 | 115.1523 | 115.5175 | 115.4292 | 108.8223 | 109.412 | 109.4115 | 108.6122 | 109.2439 | 108.3259 | 109.2048 | 102.4447 | 91.3803 | 89.2551 | 89.6276 | 89.5376 | 78.3331 | 78.9346 | 78.9341 | 78.1188 | 78.7631 | 77.8267 | 78.7232 | 71.7214 | 57.8337 | 55.6896 | 56.0654 | 55.9746 | 40.9712 | 41.5781 | 41.5776 | 40.755 | 41.4051 | 40.4603 | 41.3648 | 34.876 | 19.4307 | 17.2437 | 17.6271 | 17.5344 | 0.10363 | 0.72263 | 0.72211 | -0.11692 | 0.54618 | -0.41751 | 0.50506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 2035 | 2035-06-01 | 2036-05-31 | 10.2
[382 empty] | 8 | 2036 | 2036-06-01 | 2037-05-31 | 10
Year 1 installs | NPV | 1: 1; 2: 2; 3: 3; 4: 4; 5: 5; 6: 6; 7: 7; 8: 8; 9: 9; 10: 10; 11: 11; 12: 12; 1: 13; 2: 14; 3: 15; 4: 16; 5: 17; 6: 18; 7: 19; 8: 20; 9: 21; 10: 22; 11: 23; 12: 24; 1: 25; 2: 26; 3: 27; 4: 28; 5: 29; 6: 30 | 8 | 2037 | 2037-06-01 | 2038-05-31 | 9.8
Revenues | [381 empty] | 8 | 2038 | 2038-06-01 | 2039-05-31 | 9.7
Energy | 1551.0088 | 1: 137.1003; 2: 143.4028; 3: 138.5683; 4: 140.74; 5: 144.3251; 6: 147.4964; 7: 151.4094; 8: 153.4109; 9: 154.9568; 10: 158.056; 11: 158.104; 12: 158.1462; 1: 159.718; 2: 156.3627; 3: 154.4648; 4: 149.1115; 5: 131.3649; 6: 100.6141; 7: 57.7657; 8: 5.9172; 9: 0; 10: 0; 11: 0; 12: 0; 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0 | 8 | 2039 | 2039-06-01 | 2040-05-31 | 9.3
DASI | 72.962 | 1: 6.426; 2: 6.5545; 3: 6.6219; 4: 6.7544; 5: 6.8895; 6: 7.0273; 7: 7.0989; 8: 7.2409; 9: 7.314; 10: 7.4602; 11: 7.4602; 12: 7.4573; 1: 7.5288; 2: 7.3627; 3: 7.2677; 4: 7.0012; 5: 6.1331; 6: 4.6275; 7: 2.5349; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0
Rate 1 | 746.2692 | 1: 67.449; 2: 68.7979; 3: 68.8035; 4: 70.1796; 5: 71.5832; 6: 73.0148; 7: 73.0064; 8: 74.4665; 9: 74.4429; 10: 75.9318; 11: 75.1409; 12: 75.1108; 1: 75.8312; 2: 73.3777; 3: 71.6603; 4: 69.0328; 5: 59.8225; 6: 45.1373; 7: 24.4564; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0
Frequency | 656.2733 | 1: 191.0597; 2: 162.4008; 3: 136.726; 4: 116.2171; 5: 98.7845; 6: 83.9668; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0
T&D Deferral | 933.6836 | 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 746.75; 8: 746.75; 9: 0; 10: 0; 11: 0; 12: 0; 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0
Power Factor/VAR support | 0 | 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0; 7: 0; 8: 0; 9: 0; 10: 0; 11: 0; 12: 0; 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0
Capacity | 6457.1809 | 1: 322.17; 2: 376.95; 3: 516.66; 4: 614.83; 5: 629.6; 6: 622.03; 7: 629.15; 8: 627.69; 9: 618.72; 10: 631.58; 11: 765.62; 12: 847.92; 1: 842.37; 2: 820.07; 3: 778.04; 4: 720.99; 5: 626.81; 6: 482.77; 7: 297.89; 8: 87.8; 9: 0; 10: 0; 11: 0; 12: 0; 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0 | 8 | 2040 | 2040-06-01 | 2041-05-31 | 9
RNS | 11122.645 | 1: 1243.11; 2: 1341.08; 3: 1317.19; 4: 1296; 5: 1251.61; 6: 1197.73; 7: 1136.38; 8: 1087.12; 9: 1031.08; 10: 986.2; 11: 927.16; 12: 869.62; 1: 823.14; 2: 757.48; 3: 701.39; 4: 635.12; 5: 526.85; 6: 378.73; 7: 202.75; 8: 15.06; 9: 0; 10: 0; 11: 0; 12: 0; 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0 | 8 | 2041 | 2041-06-01 | 2042-05-31 | 8.5
Total | 21540.0227 | 1: 1967.315; 2: 2099.186; 3: 2184.5697; 4: 2244.721; 5: 2202.7922; 6: 2131.2653; 7: 2743.7946; 8: 2696.6782; 9: 1886.5137; 10: 1859.228; 11: 1933.4851; 12: 1958.2542; 1: 1908.588; 2: 1814.6531; 3: 1712.8228; 4: 1581.2555; 5: 1350.9804; 6: 1011.8789; 7: 585.397; 8: 108.7772; 9: 0; 10: 0; 11: 0; 12: 0; 1: 0; 2: 0; 3: 0; 4: 0; 5: 0; 6: 0 | 8 | 2042 | 2042-06-01 | 2043-05-31 | 7.3
(0) Adjusted for failure rate | [381 empty] | 8 | 2043 | 2043-06-01 | 2044-05-31 | 5.4
(1) Adjusted for degradation and availability | [381 empty] | 8 | 2044 | 2044-06-01 | 2045-05-31 | 2.9
(2) Adjusted for losses, reserve margin (for FCM), and forecast error. | [381 empty] | 8 | 2045 | 2045-06-01 | 2046-05-31 | 0
[382 empty] | 8 | 2046 | 2046-06-01 | 2047-05-31 | 0
[382 empty] | 8 | 2047 | 2047-06-01 | 2048-05-31 | 0
[382 empty] | 8 | 2048 | 2048-06-01 | 2049-05-31 | 0
All Year Installs (for single system calc) | [381 empty] | 8 | 2049 | 2049-06-01 | 2050-05-31 | 0
Revenues | NPV (2025 dollars) | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | [350 empty] | 8 | 2050 | 2050-06-01 | 2051-05-31 | 0
Energy | 458686.416 | 27420.0635 | 42654.0623 | 42322.6782 | 42276.3258 | 43215.9444 | 44214.2496 | 45319.625 | 46114.1611 | 46629.3238 | 47406.7443 | 47732.2571 | 47745.4988 | 48063.9543 | 47553.0224 | 46831.1119 | 45566.7603 | 41471.1795 | 33510.7613 | 21804.2701 | 7063.9436 | 591.7239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [350 empty] | 8 | 2051 | 2051-06-01 | 2052-05-31 | 0
DASI | 21582.2599 | 1285.2 | 1966.356 | 1992.9486 | 2026.313 | 2066.8393 | 2108.176 | 2136.5553 | 2172.2565 | 2201.3605 | 2238.0738 | 2252.9942 | 2252.3974 | 2266.3988 | 2240.4749 | 2204.5323 | 2141.5457 | 1940.7346 | 1551.0754 | 978.9771 | 258.5548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rate 1 | 220747.3235 | 13489.7927 | 20639.3829 | 20778.0907 | 21053.8717 | 21474.9492 | 21904.4482 | 22048.7871 | 22339.9504 | 22484.1729 | 22779.5423 | 22773.2146 | 22686.5258 | 22827.5502 | 22410.3179 | 21816.5817 | 21115.9031 | 19005.8323 | 15129.3444 | 9495.29 | 2494.5571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [350 empty] | 8 | 2052 | 2052-06-01 | 2053-05-31 | 0
Frequency | 183647.8143 | 38211.9413 | 48720.2251 | 41149.2568 | 34865.1211 | 29635.3529 | 25190.05 | 7137.1808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [350 empty] | 8 | 2053 | 2053-06-01 | 2054-05-31 | 0
T&D Deferral | 274430.8445 | 0 | 0 | 0 | 0 | 0 | 0 | 149350 | 224025 | 74675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [350 empty] | 8 | 2054 | 2054-06-01 | 2055-05-31 | 0
Power Factor/VAR support | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [350 empty] | 8 | 2055 | 2055-06-01 | 2056-05-31 | 0
Capacity | 1921808.5269 | 64434 | 100240 | 155334 | 184674 | 188880 | 186609 | 189109 | 188552 | 185973 | 189719 | 230694 | 256090 | 253922 | 248434 | 236317 | 219753 | 195379 | 157426 | 106461 | 46472 | 8505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [350 empty] | 8 | 2056 | 2056-06-01 | 2057-05-31 | 0
RNS | 3235325.4542 | 248622 | 391174 | 396312 | 388903 | 375483 | 359319 | 341926 | 326224 | 310248 | 295941 | 279853 | 262650 | 247852 | 230291 | 212798 | 194121 | 166194 | 126168 | 76794 | 22426 | 1442 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [350 empty] | 8 | 2057 | 2057-06-01 | 2058-05-31 | 0
Total | 6316228.6393 | 393462.9975 | 605394.0263 | 657888.9743 | 673798.6316 | 660756.0858 | 639344.9238 | 757027.1483 | 809427.368 | 642210.8572 | 558084.3603 | 583305.466 | 591424.4221 | 574931.9033 | 550928.8152 | 519967.2259 | 482698.2091 | 423990.7464 | 333785.1811 | 215533.5372 | 78715.0555 | 10538.7239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [350 empty] | 8 | 2058 | 2058-06-01 | 2059-05-31 | 0